## Connection Details
ADI 0002 Compliance Check list
Note: This compliance check sheet is to be completed by the connecting proponent during preliminary enquiry.
Proponent Name
Date
Check sheet shall be completed in accordance to ADI0002. All clause numbers are aligned to the Standard. Instructions: A. For non generator, high voltage customer connections: A.1 - Enter "Section 5" on the Remote Control Interface option on Table 1, and A.2 - Proceed to Tab "Section 5" - Column C will indicate if the requirement is Mandatory or Preferred B. For generator connections: B.1 - If application requires a CSIP-AUS interface, there is no requirement to complete this checksheet B.2 - Enter high level Generator details in Table 1 B.3 - Assess which Option is applicable on Tables 2 and 3. B.4 - Based on Table 3, navigate to the tab by that name and complete the assessment (i.e. "Section 5", "Section 6.3" etc) - Based on the "Remote Control Interface" Selected on Table 1, tables on the non-relevant Tab's will be greyed out B.5 - For each requirement, select if requirement is met or not in the dropdown in the blue cells, and enter any additional comments as required. B.6 - If AGC is required, complete both Section 6.3 and 6.5.
Table 1 - Gen Details
System Capacity (MVA)
Gen Unit Type
Remote Control Interface | Sections 6.3 & 6.5
Table 2 - Remote Control Interface Criteria
Production unit type | >200kVA & ≤1.5MVA | >1.5MVA & <5MW | ≥5MVA
IES | CSIP-AUS | SCADA | SCADA and AGC*
Non-IES | SCADA |  | SCADA and AGC*
Table 3 - Standard Number for Remote Control Interface
Production unit type | >200kVA & ≤1.5MVA | >1.5MVA & <5MW | ≥5MVA
IES | - | 6.3 | 6.3 and 6.5*
Non-IES | 6.3 |  | 6.3 and 6.5*

## Section 5
Remote Control Interface | Sections 6.3 & 6.5 | M | Mandatory
|  | P | Preferred
|  | n/a | not applicable
|  | A | By Agreement based on network need
| HVC | Option | Compliance | Customer Comments
Section 5 | High Voltage Customer Connection
5.2 | Requirements
5.2.2 | Minimum Remote Monitoring Requirement
5.2.2.1 | Status/Indication
5.2.2.1 (a) | Point of connection CB Position | M
5.2.2.1 (b) | All CB/switches position were a ring can be formed, | M
5.2.2.1 (c) | Protection operation alarms | M
5.2.2.1 (d) | HVC Protection System Compromised | M
5.2.2.2 | Analogues
5.2.2.2 (a) | Connection Point Active Power Output | M
5.2.2.2 (b) | Connection Point Reactive Power Output | M
5.2.2.2 (c) | Connection Point Current (three-phase Amps) | P
5.2.2.2 (d) | Connection Point Voltage (three-phase Volts) | P
5.2.2.2 (e) | Transformer Active Power Output (where under EE operational control) | A
5.2.2.2 (f) | Transformer Reactive Power Output (where under EE operational control) | A
5.2.2.2 (g) | Transformer Current (where under EE operational control) | A
5.2.2.2 (h) | Transformer Voltage (where under EE operational control) | A
5.2.3 | Minimum Control Requirements
To be agreed with HV Customer Manager during Application Stage
5.2.4 | Communication Protocol
5.2.4 (a) | DNP3 over serial (preferred), or | P
5.2.4 (b) | Modbus
5.2.5 | Physical Requirements
5.2.5.1 | Site Access
5.2.5.1 | 24 hours site access to EE’s equipment for faults and maintenance | P
5.2.5.2 | Accommodation for Endeavour Energy’s Equipment | M
5.2.5.2 (a) | A suitable location as close as practical to the customer’s generator control system | M
5.2.5.2 (b) | A 32mm ⌀ (minimum) conduit to the location of the EE equipment | M
5.2.5.2 (c) | An accommodation for the remote communications | M
5.2.5.2 (d) | compliance with AS 2067 | M
5.2.5.2 (e) | A suitably sized earth bonding | M
5.2.5.3 | Fibre/Radio Connection to Customer’s Control Room
5.2.5.3 (a) | External entry of fibres and/or coaxial cables into the customers control room | M
5.2.5.3 (b) | Pole or antenna mounting location for an EE communication equipment - ADI0006 | M
5.2.5.4 | Interface
5.2.5.4 (a) | Single point-to-point connection | M
5.2.5.4 (b) | A MMOF communication cable (or approved alternative) | P
5.2.5.4 (c) | A TCP/IP (IEEE 802.3 ) interface shall be considered on request by EE
5.2.5.5 | DC Supply
5.2.5.5 (a) | 48 Vdc backup power supply to supply the EE SCADA equipment | P
5.2.5.5 (b) | Two protected ELV feeders to dual isolators located near EE's equipment cubicle | P
5.2.5.6 | AC Supply
5.2.5.6 | RCD protected 230V socket outlet for commissioning and maintenance | M
Fibre/Radio Connection to Customer’s Control Room

## Section 6.3
System Capacity |  | M | Mandatory
Gen Unit Type |  | P | Preferred
Remote Control Interface | Sections 6.3 & 6.5 | n/a | not applicable
|  | A | By Agreement based on network constraints
Section 6 | Generator Connection | Options | Compliance | Customer Comments
6.3 | SCADA Connection Requirement
6.3.2 | Inverter Requirement
6.3.2 | Inverter can except flexible exports as per 6.1.1 - On the approved CEC list | M
6.3.3 | Minimum Remote Monitoring Requirement
6.3.3.1 | Status/Indication
6.3.3.1 (a) | Circuit Breaker position (all required) | M
6.3.3.1 (b) | Circuit Breaker Status (all required) | M
6.3.3.1 (c) | Protection operation alarms (including CB Fail) | M
6.3.3.1 (d) | HVC Protection System Compromised | M
Below are additional signals for BESS:
6.3.3.1 (e) | Export power (Discharge) Mode | M
6.3.3.1 (f) | Import power (Charging) Mode | M
6.3.3.1 (g) | Grid (Parallel) Mode | M
6.3.3.1 (h) | Island Mode | M
Below relevant for non IES generation:
6.3.3.1 (i) | Generating Unit Status (For all Generating Units) | P
6.3.3.2 | Analogues
6.3.3.2 (a) | Connection Point Active Power | M
6.3.3.2 (b) | Connection Point Reactive Power | M
6.3.3.2 (c) | Connection Point 3ph Current (Aph, Bph and Cph Amps) | P
6.3.3.2 (d) | Connection Point 3ph L-L Voltage (AB, BC and CA Volts) | P
6.3.3.2 (e) | Generating System Active Power | M
6.3.3.2 (f) | Generating System Reactive Power | M
6.3.3.2 (g) | Generating System Current (three-phase Amps) | P
6.3.3.2 (h) | Generating System Voltage (three-phase Volts) | P
6.3.3.2 (i) | Number of Generating Units Connected | P
6.3.3.2 (j) | Generating System Dispatch Limiter Feedback | M
6.3.3.2 (k) | Power System Dispatch Limiter Feedback | M
6.3.3.2 (l) | Power Factor Set Point Control Feedback (if required) | P
6.3.3.2 (m) | Charge Rate Limiter for Energy Storage Systems Acknowledged (if required) | P
6.3.3.2 (n) | Frequency Response Import/Export Limit (if required) | P
Below are additional signals for BESS:
6.3.3.2 (o) | State of Charge (%) | M
6.3.4 | Control Requirements
6.3.4.1 | Flexible Exports Setpoint Controls
6.3.4.1 (a) | Generation Dispatch Limit (GDL) Setpoint | M
6.3.4.1 (b) | Generating System Net Export Limiter Setpoint | M
6.3.4.1 (c) | Power Factor Setpoint Control (if required) | A
6.3.4.1 (d) | Charge Rate Limiter for Energy Storage Systems (if required) | M
6.3.4.1 (e) | Discharge Rate Limiter for Energy Storage Systems (if required) | M
6.3.4.1 (f) | Frequency response active import/export limit (if required) | A
6.3.5 | Communication Protocol
6.3.5 (a) | DNP3 over serial (preferred), or | P
6.3.5 (b) | Modbus
6.3.6 | Communications Signal Fail-safe
6.3.6 | Customer system supports signal fail-safe | M
6.3.7 | Physical Requirements
6.3.7.1 | Site Access
6.3.7.1 | 24 hours site access to EE’s equipment for faults and maintenance | M
6.3.7.2 | Accommodation for Endeavour Energy’s Equipment
6.3.7.2 (a) | A suitable location as close as practical to the customer’s generator control system | M
6.3.7.2 (b) | A 32mm ⌀ (minimum) conduit to the location of the EE equipment | M
6.3.7.2 (c) | An accommodation for the remote communications | M
6.3.7.2 (d) | compliance with AS 2067 | M
6.3.7.2 (e) | A suitably sized earth bonding | M
6.3.7.3 | Fibre/Radio Connection to Customer’s Control Room
6.3.7.3 (a) | External entry of fibres and/or coaxial cables into the customers control room | M
6.3.7.3 (b) | Pole or antenna mounting location for an EE communication equipment - ADI0006 | M
6.3.7.4 | Interface
6.3.7.4 (a) | Single point-to-point connection | M
6.3.7.4 (b) | A MMOF communication cable (or approved alternative) | P
6.3.7.4 (c) | A TCP/IP (IEEE 802.3 ) interface shall be considered on request by EE
6.3.7.5 | DC Supply
6.3.7.5 (a) | 48 Vdc backup power supply to supply the EE SCADA equipment | P
6.3.7.5 (b) | The DC system shall have a 24-hour survival time . | P
6.3.7.6 | AC Supply
6.3.7.6 | RCD protected 230V socket outlet for commissioning and maintenance | M

## Section 6.4 (hidden)
System Capacity |  | M | Mandatory
Export |  | P | Preferred
Generator Type | #REF! | n/a | not applicable
Remote Control Interface | Sections 6.3 & 6.5 | A | By Agreement based on network constraints
| IES | Export | Compliance | Customer Comments
Section 6 | Generator Connection | >30kVA & <1.5MVA
6.4 | CSIP-AUS Connection
6.4.2 | Proposed SIP Client Option - Select which one is applicable
6.4.2 | On-Device (CSIP software client directly on the inverter) | M
6.4.2 | Hardware Gateway - Dedicated gateway device
6.4.2 | Cloud Platform
6.4.3 | Flexible Exports Setpoint Controls and Monitoring
6.4.3.1 | Setpoint Controls
6.4.3.1 (a) | Connect/Disconnect [opModEnergize] | M
6.4.3.1 (b) | Real Power Output Limit Control [opModMaxLimW] | M
6.4.3.1 (c) | Site Export Limit (in Watts) [opModExpLimW] | M
6.4.3.1 (d) | Site Import Limit (in Watts) [opModExpLimW] | M
6.4.3.1 (e) | Max Generation Limit (in Watts) [opModGenLimW] | M
6.4.3.1 (f) | Max Load Limit (in Watts) [opModLoadLimW] | M
6.4.3.2 | Monitored parameters
6.4.3.2 (a) | Site Real (Active) Power | M
6.4.3.2 (b) | Site Reactive Power | M
6.4.3.2 (c) | Generator Real (Active) Power | M
6.4.3.2 (d) | Generator Reactive (Active) Power | M
6.4.3.2 (e) | Site Voltage (Line to Neutral) | M
6.4.3.2 (f) | Generator Voltage (Line to Neutral) | M
6.4.3.2 (g) | Frequency | M
6.4.4 | Communications Signal Fail-safe
6.4.4 | Customer system supports signal fail-safe | M
6.4.6 | Multiple Inverters
6.4.6 | All inverters within installation are controllable from CSIP-AUS client | M
Fibre/Radio Connection to Customer’s Control Room

## Section 6.5
System Capacity
Remote Control Interface | Sections 6.3 & 6.5
| IES | Compliance | Customer Comments
Section 6 | Generator Connection
6.5 | Automatic Generation Control
6.5.3 | Communications Protocol
6.5.3 | Customer controller supports ICCP TASE.2
6.5.4 | Physical Requirements
6.5.4.1 | If required, there is accommodation for EE communications equipment
6.5.4.2 | Where applicable, external entry of fibre optic cables to EE communications equipment
Note: Communication/Networking designs and Signal List agreements will be performed during the Application stage of the connection process.
Fibre/Radio Connection to Customer’s Control Room