## Main
3E - Earthing Design Tool |  |  |  |  | Sheet Version: 2.6 May 2017 |  |  |  | DESIGN INCOMPLETE - PLEASE MAKE SURE ALL VALUES ARE FILLED | ALARP DESIGN NOT ASSESSED
Online Version: 2.6 May 2017
Work Info | 1) Enter data in orange coloured fields
Location
Project Number
Designed by:
Company
Proposed Equipment
Conductive Pole?
Other:
Location Category
Soil Structure | Soil resistivity | ρ1 | 0 | Ωm | Depth (m) |  | 0
|  | ρ2 | 0 | Ωm
Supply | Zone Substation
6
Feeder number
| Feeder nominal voltage kV | [6 empty] | SEF Pickup (A)
Protection Info | Single Phase fault level at the location - kA |  |  |  | Sensitive earth fault protection available?
| EF Settings Used |  |  |  | EF Pickup (A) |  | 240
| Fuse Rating: |  | 100 |  | IEC Time Lever |  | 0.13
[5 empty] | Hi-set (Y/N) | Hi-set (A) | No
Hi-set Operate Time (s)
[5 empty] | Time Margin (Y/N) | Time Margin (s) | No
[5 empty] | Protection Curve |  | IEC SI
Earthing Configuration | Common/Separate?
Metallic return to source?
Earthgrid Details | HV Earth Grid |  |  | FALSE | LV Earth Grid
| Radius "r" of rod/s (mm) |  |  |  | Neutral bond to 1 other DS? |  | Yes |  |  |  | 0 | 0
| Length of bare "L" rod/s (m) |  |  |  | Length "L" of rod/s (m) |  | 2.4 |  |  |  | 0 | 0
| Insulated conductor depth "h" (m) |  |  |  | Number of rods |  | 2 |  |  |  | 0 | 0
| Number of rods |  |  |  | LV resistance in (Ω) |  | #DIV/0! |  |  |  | 0 | 0
| Combined HV rod resistance (Ω) |  | #DIV/0! |  | LV with MEN (Ω) |  | #DIV/0!
| Commissioning Check (Ω) | No |  |  | Satisfactory? |  | #DIV/0!
MEN Details | Number of connected Customers |  |  |  | MEN Type
| MEN Impedance (Ω) |  | #DIV/0!
| F Factor |  | 1
Constraints | Metallic MEN connected infrastructure near location? |  |  | EPR at asset:
| Fences near location? |  |  | EPR at fence:
| Communications assets near location? |  |  | EPR at asset:
| Metallic pipelines near location? |  |  | EPR at asset:
| Single metallic object (touch voltage) |  |  | Touch voltage at asset: |  | Distance to asset (m):
Fault Clearance | Total fault current seen by protection (A) |  | #DIV/0!
| Minimum current seen by SEF (A) |  | #DIV/0! |  | EF Clearing Time (s) |  | #DIV/0! | #DIV/0!
| Maximum fault current through soil (A) |  | #DIV/0! |  | HV Fuse Trip Time |  | Not fused | Not fused
[5 empty] | SEF Operates? |  | #DIV/0!
Maximum allowable voltage limits | MEN limit (V) |  | #DIV/0! |  | User Defined Criteria (V)
| Backyard (V) |  | #DIV/0! |  | User Defined Criteria note:
| Urban (V) |  | #DIV/0!
| Aquatic Centre (V) |  | #DIV/0!
| Backyard Step Voltage (V) |  | #DIV/0!
| Urban Step Voltage(V) |  | #DIV/0!
| EPR Limit (Common earthed) |  | #DIV/0! | Note: EPR values will be false until all information is provided
Ratings | 95mm2 Aluminium |  | #DIV/0! |  | 50mm2 AAAC XLPE |  | #DIV/0!
| 70mm2 Copper |  | #DIV/0!
Results | EPR (V) |  | #DIV/0!
| Distance to 430V Contour (m) |  | #VALUE! |  | Touch Voltage to asset(V) |  | #DIV/0!
| Distance to MEN limit (m) |  | #VALUE! |  | Max Step Voltage (V) |  | #VALUE!
| Distance to Backyard limit (m) |  | #VALUE!
| Distance to Urban limit (m) |  | #VALUE! |  | Satisfactory?
| Min HV/LV electrode separation |  | #VALUE! |  | Argon Used?
Design notes:
|  |  | Checks for common | Checks for separate |  |  |  | Checks for separate (LBS+Recloser)
|  |  | FALSE | FALSE | Location |  |  | FALSE | Location
|  |  | FALSE | FALSE | Project Number |  |  | FALSE | Project Number
|  |  | FALSE | FALSE | Company |  |  | FALSE | Company
|  |  | FALSE | FALSE | Proposed Equipment |  |  | FALSE | Proposed Equipment
|  |  | FALSE | FALSE | Conductive Pole? |  |  | FALSE | Conductive Pole?
|  |  | FALSE | FALSE | Location Category |  |  | FALSE | Location Category
|  |  | FALSE | FALSE | Feeder number |  |  | FALSE | Feeder number
|  |  | FALSE | FALSE | Feeder nominal voltage kV |  |  | FALSE | Feeder nominal voltage kV
|  |  | FALSE | FALSE | Sensitive earth fault protection available? |  |  | FALSE | Sensitive earth fault protection available?
|  |  | FALSE | FALSE | Single Phase fault level at the location - kA |  |  | FALSE | Single Phase fault level at the location - kA
|  |  | FALSE | FALSE | EF Settings Used |  |  | FALSE | EF Settings Used
|  |  | FALSE | FALSE | Common/Separate? |  |  | FALSE | Common/Separate?
|  |  | FALSE | FALSE | Metallic return to source? |  |  | FALSE | Metallic return to source?
|  |  | FALSE | FALSE | Radius "r" of rod/s (mm) |  |  | FALSE | Radius "r" of rod/s (mm)
|  |  | FALSE | FALSE | Length of bare "L" rod/s (m) |  |  | FALSE | Length of bare "L" rod/s (m)
|  |  | FALSE | FALSE | Number of rods |  |  | FALSE | Number of rods
|  |  | FALSE | FALSE | Number of connected Customers |  |  | FALSE | Number of connected Customers
|  |  | FALSE | FALSE | Dense Urban |  |  | FALSE | Dense Urban
|  | Zone Substation | FALSE | TRUE | Neutral bond to 1 other DS? |  |  | FALSE | Zone Substation
|  | Designed by: | FALSE | TRUE | Length "L" of rod/s (m) |  |  | FALSE | Designed by:
|  |  |  | TRUE | Number of rods
|  |  |  | FALSE | Designed by:
|  |  | FALSE | FALSE |  |  |  | FALSE
|  |  | FALSE | FALSE |  |  |  | FALSE
|  |  |  | FALSE |  |  |  | FALSE
|  |  | FALSE | FALSE | Sensitive earth fault protection available?
|  |  |  | TRUE | EF Pickup (A)
|  |  |  | TRUE | IEC Time Lever
|  |  |  | TRUE | Protection Curve
|  |  |  | TRUE | Hi-set (Y/N)
|  |  |  | TRUE | Time Margin (Y/N)
FALSE
Help Page

## ALARP Design
ALARP DESIGN
Have you considered moving the asset to reduce/remove the risk by placement of the asset or use of alternative material? | FALSE
Comments: (if applicable)
Are the risk controls implemented reasonable in relation to industry practice; and Have you identified all reasonable additional controls in the form of risk reduction measures? | FALSE
Comments: (if applicable)
For additional information please refer to: EDI 001 - 5.2.2 EDI 001 - 5.2.4 EDI 100 - Annexure 11
FALSE

## Circuit Overview
0 | Design
DBZS/CMEN? | 0
|  | Z_Source | #DIV/0! | Ohms |  |  | Fault Current | #DIV/0! | Amps
[7 empty] | Protection Current | #DIV/0! | Amps
[7 empty] | MEN Voltage Limit | #DIV/0! | Volts
[7 empty] | EPR below limit? | N/A
[7 empty] | HV - LV separation | #VALUE! | metres
| Voltage | [5 empty] | Head Room (%) |  | #DIV/0!
0
kV
EPR
#DIV/0!
V
|  | Metallic Return Current |  | 0 | Amps
[6 empty] | HV grid |  | LV grid |  | MEN
[6 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[6 empty] | Ohms |  | Ohms |  | Ohms
[6 empty] | Current |  |  |  | Current
[6 empty] | #DIV/0! |  |  |  | 0
[6 empty] | Amps |  |  |  | Amps

## Soil Model
Soil Resistivity Calculator
PROJECT NO. | TEST LOCATION |  | DATE | TIME
LATITUDE OF TEST |  | LONGITUDE OF TEST
TEMPERATURE (⁰C) | SOIL TYPE | SOIL CONDITION | METER MODEL | METER SERIAL NO.
ELECTRODE SPACING (m) | TEST APPLIED 1 (Ω) | TEST APPLIED 2 (Ω) | TEST APPLIED 3 (Ω) | AVERAGE (Ω)
0
ELECTRODE SPACING (m) | SOIL RESISTIVITY (Ω.m) |  | Soil Model |  |  | Model | Error(%)^2
#N/A | #N/A |  | Layer | Resistivity (Ω.m) | Depth (m) - h | 0 | 0
#N/A | #N/A |  | 1 |  |  | 0 | 0
#N/A | #N/A |  | 2 |  | Infinity | 0 | 0
#N/A | #N/A |  | Error(%) | 0 |  | 0 | 0
#N/A | #N/A |  |  |  |  | 0 | 0
#N/A | #N/A |  |  |  |  | 0 | 0
#N/A | #N/A |  |  |  |  | 0 | 0
#N/A | #N/A |  |  |  |  | 0 | 0
[6 empty] | Total | 0 | RMS Error
WARNING: A minimum of 5 test spacings must be used to accurately determine a model
[7 empty] | Soil Model |  | s | pa(s)
[7 empty] | p1 | 0 | 0.5 | #VALUE!
[7 empty] | p2 | 0 | 1 | #VALUE!
[9 empty] | 1.5 | #VALUE!
[7 empty] | K | #DIV/0! | 2 | #VALUE!
[9 empty] | 2.5 | #VALUE!
[9 empty] | 3 | #VALUE!
[9 empty] | 3.5 | #VALUE!
[9 empty] | 4 | #VALUE!
[9 empty] | 4.5 | #VALUE!
[9 empty] | 5 | #VALUE!
[9 empty] | 5.5 | #VALUE!
[9 empty] | 6 | #VALUE!
[9 empty] | 6.5 | #VALUE!
[9 empty] | 7 | #VALUE!
[9 empty] | 7.5 | #VALUE!
[9 empty] | 8 | #VALUE!
[9 empty] | 8.5 | #VALUE!
[9 empty] | 9 | #VALUE!
[9 empty] | 9.5 | #VALUE!
[9 empty] | 10 | #VALUE!
[9 empty] | 10.5 | #VALUE!
[9 empty] | 11 | #VALUE!
[9 empty] | 11.5 | #VALUE!
[9 empty] | 12 | #VALUE!
[9 empty] | 12.5 | #VALUE!
[9 empty] | 13 | #VALUE!
[9 empty] | 13.5 | #VALUE!
[9 empty] | 14 | #VALUE!
[9 empty] | 14.5 | #VALUE!
[9 empty] | 15 | #VALUE!
[9 empty] | 15.5 | #VALUE!
[9 empty] | 16 | #VALUE!
[9 empty] | 16.5 | #VALUE!
[9 empty] | 17 | #VALUE!
[9 empty] | 17.5 | #VALUE!
[9 empty] | 18 | #VALUE!
[9 empty] | 18.5 | #VALUE!
[9 empty] | 19 | #VALUE!
[9 empty] | 19.5 | #VALUE!
[9 empty] | 20 | #VALUE!
[9 empty] | 21 | #VALUE!
[9 empty] | 22 | #VALUE!
[9 empty] | 23 | #VALUE!
[9 empty] | 24 | #VALUE!
[9 empty] | 25 | #VALUE!
[9 empty] | 26 | #VALUE!
[9 empty] | 27 | #VALUE!
[9 empty] | 28 | #VALUE!
[9 empty] | 29 | #VALUE!
[9 empty] | 30 | #VALUE!
[9 empty] | 31 | #VALUE!
[9 empty] | 32 | #VALUE!
[9 empty] | 33 | #VALUE!
[9 empty] | 34 | #VALUE!
[9 empty] | 35 | #VALUE!
[9 empty] | 36 | #VALUE!
[9 empty] | 37 | #VALUE!
[9 empty] | 38 | #VALUE!
[9 empty] | 39 | #VALUE!
[9 empty] | 40 | #VALUE!
[9 empty] | 41 | #VALUE!
[9 empty] | 42 | #VALUE!
[9 empty] | 43 | #VALUE!
[9 empty] | 44 | #VALUE!
[9 empty] | 45 | #VALUE!
[9 empty] | 46 | #VALUE!
[9 empty] | 47 | #VALUE!
[9 empty] | 48 | #VALUE!
[9 empty] | 49 | #VALUE!
[9 empty] | 50 | #VALUE!
Note on K74: Terry Niemeier: Soil Model assuming 2 layer
Note on L78: Terry Niemeier: Reflection Factor K
Note on K79: Terry Niemeier: Can only change h by integer using control, so this is used to allow 0.1 incrementation
Calculate Soil Model
Export soil resistivity
View location

## Protection (hidden)
| Max t (If min) | Min t (If max)
Clearing time | #VALUE! | #VALUE!
User input settings |  | Relay
Pickup | 240 | IEC SI
Time Lever | 0.13
IEF Setting | 13100
SI | #VALUE! | #VALUE!
VI | #VALUE! | #VALUE!
EI | #VALUE! | #VALUE!
Clearance time | #VALUE! | #VALUE!
SEF (User) | 10000 | 10000
Default Protection settings |  |  |  | Minimum Fault Current |  |  | Maximum Fault Current
Fault Current |  |  | Clearance Time | T/F | Interpolation | Time | T/F | Interpolation
7000 | to | ∞ | 0.6 | #DIV/0! | 0.6 | #DIV/0! | #DIV/0! | 0.6 | #DIV/0!
5000 | to | 6999 | 0.7 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
4000 | to | 4999 | 0.8 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
3000 | to | 3999 | 0.9 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2000 | to | 2999 | 1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1500 | to | 1999 | 1.5 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1000 | to | 1499 | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
500 | to | 999 | 3 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | to | 499 | 10 | #DIV/0! | 10 | #DIV/0! | #DIV/0! | 10 | #DIV/0!
|  |  |  | Clearing Time |  | #DIV/0! | Clearing Time |  | #DIV/0!
User input settings | [5 empty] | 0
Pickup | 240
Time Lever | 0.13
IEF Setting | 13100
IEC SI | #VALUE! | #VALUE!
IEC VI | #VALUE! | #VALUE!
IEC EI | #VALUE! | #VALUE!
Areva SI | #VALUE! | #VALUE!
Areva VI | #VALUE! | #VALUE!
Areva EI | #VALUE! | #VALUE!
Basler SI | #VALUE! | #VALUE!
Basler VI | #VALUE! | #VALUE!
Basler EI | #VALUE! | #VALUE!
GE SI | #VALUE! | #VALUE!
GE VI | #VALUE! | #VALUE!
GE EI | #VALUE! | #VALUE!
NOJA SI | #VALUE! | #VALUE!
NOJA VI | #VALUE! | #VALUE!
NOJA EI | #VALUE! | #VALUE!
NOJA ANSI STI | #VALUE! | #VALUE!
NULEC SI | #VALUE! | #VALUE!
NULEC VI | #VALUE! | #VALUE!
NULEC EI | #VALUE! | #VALUE!
SEL SI | #VALUE! | #VALUE!
SEL VI | #VALUE! | #VALUE!
SEL EI | #VALUE! | #VALUE!
Basler CO-2 | #VALUE! | #VALUE!
Basler CO-6 | #VALUE! | #VALUE!
Basler CO-7 | #VALUE! | #VALUE!
Basler CO-8 | #VALUE! | #VALUE!
Basler CO-9 | #VALUE! | #VALUE!
CDG33 1.55 sec | #VALUE! | #VALUE!
CDG31 3 sec | #VALUE! | #VALUE!

## Safety Criteria (hidden)
Rho |  |  | 0
Applicable Soil Res |  |  | 5 | [10 empty] | 5
Clearing Time |  |  | #DIV/0!
TDMEN Limit |  |  | #DIV/0! | [5 empty] | Backyard Limit |  |  |  |  | #DIV/0! |  |  |  |  | Urban |  |  |  |  | #DIV/0! |  |  |  | AQ12 limiy |  | #DIV/0! | School Limit |  | #DIV/0! | Urban Step Voltage |  |  |  |  | #DIV/0! |  | Backyard Step Voltage |  |  |  |  | #DIV/0!
| #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 5 | 50 | 100 | 200 | 500 | 1000 | 2000 | 5000 | Time | 5 | 50 | 100 | 200 | 500 | 1000 | 2000 | 5000 | Asphalt |  | 5 | 50 | 100 | 200 | 500 | 1000 | 2000 | 5000 | Time | 50 |  | Time |  |  |  | 5 | 50 | 100 | 200 | 500 | 1000 |  | 5 | 50 | 100 | 200 | 500 | 1000
0.01 | 665.1267 | 729.5419 | 818.5752 | 983.6586 | 1455.1858 | 2254.3669 | 3916.8834 | 8184.3864 | 0.01 | 1182.9263 | 1296.8918 | 1422.0262 | 1632.8631 | 2254.3669 | 3257.9256 | 5046.0016 | 9839.0247 | 3333.8881 | 0.01 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 6352.9192 | 9396.5893 | 15957.3022 | 0.01 | 353.1344 |  | 0.01 | 897.3933 |  | 0.01 | 39171.5891 | 50462.1827 | 63528.485 | 91826.6638 | 174972.5126 | 311149.5524 | 0.01 | 23603.3278 | 30406.982 | 39171.5891 | 56620.195 | 107886.6406 | 196321.9179
0.02 | 650.2616 | 712.8187 | 800.0265 | 961.4002 | 1422.1921 | 2203.0433 | 3827.9837 | 7997.9483 | 0.02 | 1156.2931 | 1267.781 | 1358.3424 | 1595.7657 | 2203.0433 | 3183.6898 | 4931.4401 | 9839.0247 | 3333.8881 | 0.02 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 6208.1135 | 8974.0864 | 15594.5247 | 0.02 | 353.1344 |  | 0.02 | 876.9538 |  | 0.02 | 38279.4718 | 48191.1976 | 62082.1853 | 89736.2725 | 170988.8326 | 304066.7276 | 0.02 | 23066.1972 | 29714.8353 | 38279.4718 | 55331.2366 | 105431.4009 | 191852.9048
0.03 | 635.3966 | 696.7149 | 781.4778 | 939.76 | 1390.1149 | 2152.6362 | 3740.9169 | 7815.3943 | 0.03 | 1156.2931 | 1238.6703 | 1327.4279 | 1559.2866 | 2152.6362 | 3111.2869 | 4818.7116 | 9396.2342 | 3333.8881 | 0.03 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 5928.5834 | 8769.7087 | 15239.5155 | 0.03 | 345.0961 |  | 0.03 | 857.1337 |  | 0.03 | 37408.2816 | 47094.4591 | 60669.2141 | 85697.3294 | 163293.0872 | 297145.1663 | 0.03 | 22540.6928 | 29714.8353 | 37408.2816 | 54071.7312 | 103031.6523 | 187486.0251
0.04 | 635.3966 | 680.6111 | 763.5474 | 918.1199 | 1358.0377 | 2104.0622 | 3655.6832 | 7637.5013 | 0.04 | 1129.6598 | 1210.7983 | 1297.1316 | 1524.0441 | 2104.0622 | 3040.717 | 4709.649 | 9182.6072 | 3333.8881 | 0.04 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 5793.8591 | 8569.9134 | 14892.2745 | 0.04 | 345.0961 |  | 0.04 | 837.3136 |  | 0.04 | 36556.4684 | 46022.5232 | 59288.0211 | 83747.2276 | 159576.1541 | 290381.5087 | 0.04 | 22027.5897 | 29714.8353 | 36556.4684 | 52840.9039 | 100685.4478 | 183218.5913
0.05 | 620.5315 | 680.6111 | 746.2353 | 897.098 | 1326.8769 | 2055.4881 | 3572.2824 | 7464.2692 | 0.05 | 1104.2653 | 1182.9263 | 1267.4537 | 1455.4139 | 2055.4881 | 2971.0636 | 4602.4194 | 8973.6411 | 3333.8881 | 0.05 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 5661.8842 | 8374.7006 | 14892.2745 | 0.05 | 337.2407 |  | 0.05 | 818.1129 |  | 0.05 | 34911.7482 | 44974.6147 | 56620.195 | 81840.5303 | 155943.918 | 277311.7786 | 0.05 | 21526.1128 | 29038.1903 | 35724.8074 | 51637.9794 | 98393.7609 | 179047.9155
0.06 | 620.5315 | 665.1267 | 729.5414 | 876.6945 | 1296.6327 | 2008.747 | 3490.7146 | 7127.9038 | 0.06 | 1104.2653 | 1156.2931 | 1239.0124 | 1422.0262 | 2008.747 | 2904.1597 | 4602.4194 | 8769.336 | 3333.8881 | 0.06 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 5532.6589 | 8184.0703 | 14892.2745 | 0.06 | 329.5642 |  | 0.06 | 799.5316 |  | 0.06 | 34116.5159 | 43950.7337 | 55331.2366 | 79978.0125 | 152394.4319 | 270999.6587 | 0.06 | 21036.2621 | 28377.0469 | 34911.7482 | 50462.1827 | 96154.6446 | 174971.982
0.07 | 606.9052 | 650.2616 | 712.8476 | 856.9092 | 1267.3049 | 1962.9224 | 3333.9945 | 6965.5473 | 0.07 | 1078.8709 | 1129.6598 | 1210.571 | 1389.8751 | 1962.9224 | 2838.1723 | 4602.4194 | 8569.6919 | 3333.8881 | 0.07 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 5407.0995 | 7998.0224 | 14892.2745 | 0.07 | 329.5642 |  | 0.07 | 781.5697 |  | 0.07 | 33339.8855 | 42950.8803 | 54071.7312 | 78157.3491 | 148925.7486 | 264830.6601 | 0.07 | 20557.2626 | 27731.4051 | 34116.5159 | 49313.5138 | 93965.1782 | 170989.4469
0.08 | 606.9052 | 635.3966 | 696.7721 | 837.7422 | 1238.8937 | 1918.9308 | 3257.9256 | 6965.5473 | 0.08 | 1054.0958 | 1129.6598 | 1182.748 | 1358.3424 | 1874.9392 | 2773.1014 | 4497.0229 | 8374.7087 | 3333.8881 | 0.08 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 5164.2291 | 7998.0224 | 14892.2745 | 0.08 | 322.0624 |  | 0.08 | 763.6077 |  | 0.08 | 32581.082 | 41017.8302 | 52840.9039 | 74639.2599 | 142223.0026 | 258802.767 | 0.08 | 20089.1141 | 27099.7147 | 33339.8855 | 48191.1976 | 91826.3354 | 167096.9505
0.09 | 606.9052 | 635.3966 | 680.6965 | 818.5752 | 1238.8937 | 1874.9392 | 3183.6898 | 6807.0749 | 0.09 | 1030.5594 | 1104.2653 | 1156.1615 | 1327.4279 | 1831.864 | 2709.8634 | 4395.2922 | 8184.3864 | 3333.8881 | 0.09 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 5046.0016 | 7815.6405 | 14892.2745 | 0.09 | 314.7314 |  | 0.09 | 746.2651 |  | 0.09 | 31839.3302 | 40083.8585 | 51637.9794 | 72940.2841 | 138985.0457 | 252911.9478 | 0.09 | 19631.8168 | 26482.7508 | 32581.082 | 47094.4591 | 89736.169 | 159576.6986
0.1 | 606.9052 | 620.5315 | 665.2393 | 800.0265 | 1210.4824 | 1831.864 | 3111.2869 | 6501.0056 | 0.1 | 1007.0231 | 1078.8709 | 1156.1615 | 1297.1316 | 1790.6219 | 2648.4584 | 4295.3946 | 7997.9483 | 3333.8881 | 0.1 | 5045.9839 | 5045.9839 | 5046.4421 | 5046.4421 | 5046.0016 | 5046.0016 | 7637.8411 | 14892.2745 | 0.1 | 314.7314 |  | 0.1 | 729.5419 |  | 0.1 | 30406.982 | 40083.8585 | 49313.5138 | 71280.0623 | 135822.0505 | 241528.7645 | 0.1 | 18748.2253 | 25880.5135 | 31839.3302 | 46022.5232 | 87693.7055 | 155944.2396
0.2 | 504.7079 | 540.6318 | 579.297 | 649.782 | 897.0422 | 1390.1149 | 2360.6799 | 5046.0115 | 0.2 | 763.6077 | 818.1129 | 876.6945 | 1030.0304 | 1358.0377 | 1962.9224 | 3257.9256 | 6208.1424 | 3333.8881 | 0.2 | 4197.4367 | 4197.4367 | 4295.2198 | 4497.4006 | 5046.0016 | 5046.0016 | 5928.5834 | 11560.47 | 0.2 | 255.8232 |  | 0.2 | 620.5315 |  | 0.2 | 27731.4051 | 30406.982 | 38279.4718 | 52840.9039 | 100685.4478 | 179047.9155 | 0.2 | 14553.4912 | 19631.8168 | 25291.4525 | 34911.7482 | 66522.3739 | 118295.945
0.3 | 409.9431 | 439.6733 | 471.0962 | 540.963 | 746.7375 | 1054.6788 | 1790.6219 | 3917.2841 | 0.3 | 620.5315 | 650.2616 | 680.6965 | 781.4778 | 1078.5076 | 1523.9227 | 2529.3145 | 5046.0115 | 3333.8881 | 0.3 | 4102.0526 | 4102.0526 | 4101.695 | 4197.53 | 4197.33 | 4395.2922 | 5046.0016 | 8569.6919 | 0.3 | 203.2076 |  | 0.3 | 528.2442 |  | 0.3 | 20557.2625 | 27731.4051 | 29714.8354 | 40083.8585 | 76378.3798 | 135821.2496 | 0.3 | 11297.3792 | 14892.2012 | 19185.3706 | 27731.4051 | 50462.0687 | 89736.1892
0.4 | 333.1403 | 357.296 | 374.0247 | 419.7782 | 566.1885 | 837.4702 | 1326.8769 | 2837.4967 | 0.4 | 540.6318 | 579.6526 | 620.7224 | 665.2393 | 818.2239 | 1210.4824 | 1918.9308 | 4101.3917 | 3257.7592 | 0.4 | 4102.0526 | 4102.0526 | 4101.695 | 4101.695 | 4197.33 | 4295.3946 | 4602.4194 | 6965.5473 | 0.4 | 147.2109 |  | 0.4 | 419.8532 |  | 0.4 | 15957.9365 | 20557.2625 | 26482.7508 | 31114.6302 | 57938.7701 | 103031.0162 | 0.4 | 9615.4551 | 11560.1314 | 14553.4912 | 20557.2626 | 37408.0205 | 66522.3166
0.5 | 258.815 | 271.2026 | 290.5555 | 325.7981 | 419.5498 | 592.7668 | 961.1966 | 2056.0102 | 0.5 | 429.7632 | 449.5833 | 481.6072 | 528.5972 | 696.3304 | 918.1215 | 1455.1858 | 3041.0249 | 3111.716 | 0.5 | 4102.0526 | 4102.0526 | 4101.695 | 4101.695 | 4197.33 | 4295.3946 | 4602.4194 | 5283.7201 | 0.5 | 106.6449 |  | 0.5 | 333.1403 |  | 0.5 | 12387.142 | 15594.4239 | 19185.3706 | 27731.4051 | 41972.8972 | 74639.2433 | 0.5 | 7637.4504 | 9396.8825 | 10788.9265 | 14892.2012 | 28377.567 | 48191.3667
0.6 | 196.2579 | 205.5486 | 220.0705 | 241.7106 | 318.7357 | 429.6312 | 680.75 | 1455.5241 | 0.6 | 341.1922 | 357.296 | 374.0247 | 409.8855 | 528.6124 | 729.3241 | 1129.8311 | 2254.1007 | 2306.9249 | 0.6 | 4102.0526 | 4102.0526 | 4101.695 | 4101.695 | 4197.33 | 4295.3946 | 4602.4194 | 5046.0115 | 0.6 | 82.7828 |  | 0.6 | 252.6212 |  | 0.6 | 10068.877 | 12387.142 | 14892.2012 | 20557.2625 | 31839.4356 | 54071.435 | 0.6 | 6652.3234 | 7815.7188 | 8769.0675 | 11040.0525 | 20089.9161 | 34117.0997
0.7 | 155.9983 | 163.4309 | 171.2256 | 191.6292 | 247.2493 | 333.3996 | 516.698 | 1078.7638 | 0.7 | 277.3963 | 283.5901 | 297.3567 | 325.7981 | 401.22 | 553.3577 | 837.4702 | 1709.5461 | 1790.3359 | 0.7 | 3334.0245 | 3334.0245 | 3411.6834 | 3411.6834 | 3490.7146 | 3572.2824 | 3740.9169 | 5046.0115 | 0.7 | 68.8557 |  | 0.7 | 200.5935 |  | 0.7 | 10068.877 | 10068.877 | 12105.0128 | 15957.9365 | 29714.2221 | 40083.8471 | 0.7 | 5406.7695 | 6965.4558 | 8183.8819 | 9839.4533 | 15239.7954 | 27100.1242
0.8 | 132.462 | 139.2752 | 145.2574 | 159.4781 | 206.0072 | 277.4936 | 419.5498 | 876.7891 | 0.8 | 225.3686 | 235.898 | 247.2752 | 270.7703 | 333.3996 | 439.7126 | 650.5058 | 1358.4209 | 1389.494 | 0.8 | 1267.781 | 1296.8918 | 1327.4279 | 1389.8751 | 1559.6659 | 1831.864 | 2306.6069 | 3917.2841 | 0.8 | 61.3677 |  | 0.8 | 163.4309 |  | 0.8 | 8973.6887 | 10068.877 | 10068.877 | 13582.3157 | 23065.9937 | 31839.9255 | 0.8 | 4295.3045 | 5533.1076 | 6965.4558 | 8183.8819 | 13581.8758 | 22027.717
0.9 | 118.2163 | 121.3132 | 126.7087 | 139.0745 | 174.8464 | 241.7504 | 365.4768 | 764.1494 | 0.9 | 196.2579 | 205.5486 | 210.1779 | 230.5814 | 283.909 | 365.4768 | 553.3577 | 1130.0342 | 1155.6695 | 0.9 | 1104.2653 | 1104.2653 | 1129.5751 | 1156.1615 | 1267.3049 | 1422.1921 | 1709.9706 | 3183.9608 | 0.9 | 55.968 |  | 0.9 | 145.4689 |  | 0.9 | 7997.8627 | 9396.8825 | 10068.877 | 11829.8593 | 18321.9877 | 29714.6077 | 0.9 | 3572.1546 | 4602.2362 | 5661.7709 | 7997.8627 | 11297.0036 | 18748.6936
1 | 107.6869 | 113.2613 | 118.0526 | 126.7087 | 159.2661 | 220.671 | 333.3996 | 681.0291 | 1 | 175.1991 | 178.9153 | 187.3011 | 205.8498 | 247.2493 | 326.0676 | 481.8713 | 983.9911 | 1006.519 | 1 | 781.5697 | 781.5697 | 800.0265 | 837.7422 | 939.2008 | 1078.5076 | 1422.1921 | 2647.9512 | 1 | 52.2324 |  | 1 | 132.462 |  | 1 | 7997.8627 | 8183.8819 | 9839.4533 | 10302.9513 | 15957.2862 | 27731.0674 | 1 | 3183.8394 | 4008.5248 | 4931.6453 | 6807.3395 | 10068.4102 | 16709.383
1.1 | 100.8737 | 105.2094 | 110.6332 | 121.1441 | 149.1847 | 206.0072 | 311.4038 | 635.1964 | 1.1 | 159.7146 | 167.1471 | 174.9353 | 187.3011 | 225.2535 | 296.7399 | 439.7126 | 876.7891 | 917.9609 | 1.1 | 650.2616 | 650.2616 | 665.2393 | 696.7721 | 781.5642 | 939.2008 | 1238.8937 | 2360.5258 | 1.1 | 49.8816 |  | 1.1 | 123.7907 |  | 1.1 | 7997.8627 | 8183.8819 | 8973.6887 | 10068.877 | 14892.2456 | 24153.0347 | 1.1 | 2904.0355 | 3655.8633 | 4497.6004 | 6208.2025 | 10068.4102 | 15594.6494
1.2 | 95.9187 | 100.8737 | 105.6868 | 115.5795 | 141.8527 | 192.2598 | 296.7399 | 606.4539 | 1.2 | 149.1852 | 155.9983 | 163.1878 | 174.9353 | 215.1721 | 277.4936 | 410.3849 | 818.5272 | 856.5917 | 1.2 | 606.9052 | 606.9052 | 620.7224 | 649.782 | 729.3241 | 876.8793 | 1156.4094 | 2103.3966 | 1.2 | 47.6365 |  | 1.2 | 118.2163 |  | 1.2 | 7997.8627 | 7997.8627 | 8374.5517 | 10068.877 | 14222.4578 | 22027.717 | 1.2 | 2710.2654 | 3411.713 | 4197.6444 | 5793.5345 | 9396.6753 | 14892.4815
1.3 | 94.0606 | 95.9187 | 100.7405 | 110.6332 | 135.4373 | 183.0949 | 283.909 | 579.265 | 1.3 | 145.4689 | 149.1852 | 155.7683 | 166.8976 | 200.5082 | 264.6627 | 382.8901 | 781.2396 | 799.8834 | 1.3 | 528.2442 | 540.6318 | 553.3288 | 566.3129 | 634.9254 | 746.7375 | 1007.0212 | 1918.5121 | 1.3 | 45.4925 |  | 1.3 | 113.2613 |  | 1.3 | 7637.4504 | 7997.8627 | 8183.8819 | 10068.877 | 13898.2727 | 21526.4564 | 1.3 | 2648.259 | 3258.2471 | 3917.0653 | 5406.7695 | 8973.1903 | 13898.6956
1.4 | 89.725 | 94.0606 | 98.2674 | 108.16 | 132.6878 | 179.4289 | 277.4936 | 566.0589 | 1.4 | 139.2752 | 142.372 | 148.9671 | 159.4781 | 195.9258 | 252.7483 | 373.7252 | 746.2825 | 764.1494 | 1.4 | 470.6421 | 481.7909 | 481.6072 | 504.4839 | 553.3577 | 650.5058 | 876.8793 | 1709.5461 | 1.4 | 44.457 |  | 1.4 | 110.1644 |  | 1.4 | 7463.8324 | 7997.8627 | 8183.8819 | 9839.4533 | 13581.8758 | 20089.196 | 1.4 | 2528.8966 | 3111.757 | 3827.9311 | 5164.1694 | 8570.1494 | 13582.2161
1.5 | 89.725 | 91.5831 | 96.4125 | 105.6868 | 129.9383 | 174.8464 | 264.6627 | 540.4237 | 1.5 | 135.5589 | 139.2752 | 145.2574 | 152.6769 | 187.6773 | 241.7504 | 357.2284 | 712.879 | 746.2825 | 1.5 | 419.8532 | 429.7632 | 439.5634 | 449.4561 | 492.8692 | 579.0194 | 799.894 | 1596.1295 | 1.5 | 43.445 |  | 1.5 | 105.2094 |  | 1.5 | 7294.0898 | 7997.8627 | 8183.8819 | 9396.8825 | 12675.5204 | 18748.6936 | 1.5 | 2471.5407 | 3040.4496 | 3655.8633 | 4931.6453 | 8374.4701 | 13273.1278
1.6 | 85.3893 | 89.725 | 93.9393 | 100.7405 | 127.1889 | 171.1805 | 259.1637 | 528.7713 | 1.6 | 129.9845 | 135.5589 | 139.0745 | 148.9671 | 183.0949 | 236.2514 | 348.9799 | 696.5656 | 729.1923 | 1.6 | 382.6905 | 382.6905 | 391.9551 | 409.8855 | 449.7941 | 528.6124 | 746.7375 | 1488.9276 | 1.6 | 42.4561 |  | 1.6 | 105.2094 |  | 1.6 | 7128.2227 | 7815.7188 | 8183.8819 | 8973.6887 | 12105.0326 | 18322.0174 | 1.6 | 2359.9292 | 2971.4675 | 3572.1546 | 4819.2587 | 8374.4701 | 12675.7811
1.7 | 85.3893 | 89.725 | 92.0845 | 100.7405 | 123.5229 | 167.5145 | 252.7483 | 516.3421 | 1.7 | 126.8876 | 132.462 | 135.9831 | 145.2574 | 179.4289 | 230.7525 | 340.7315 | 681.0291 | 712.879 | 1.7 | 349.2441 | 349.2441 | 357.3309 | 374.0247 | 410.3849 | 492.8692 | 696.3304 | 1389.494 | 1.7 | 41.4897 |  | 1.7 | 102.7319 |  | 1.7 | 6965.4558 | 7637.4504 | 8183.8819 | 8569.8719 | 11559.8564 | 17496.8861 | 1.7 | 2306.4486 | 2904.0355 | 3490.7712 | 4709.1973 | 8374.4701 | 12386.8508
1.8 | 83.5312 | 87.8668 | 89.6113 | 98.2674 | 120.7734 | 162.9321 | 252.7483 | 504.6897 | 1.8 | 123.7907 | 129.9845 | 135.9831 | 145.2574 | 174.8464 | 225.2535 | 333.3996 | 665.4926 | 696.5656 | 1.8 | 318.2753 | 325.7078 | 333.2176 | 341.2553 | 382.8901 | 470.8734 | 665.1697 | 1327.3479 | 1.8 | 41.4897 |  | 1.8 | 100.8737 |  | 1.8 | 6965.4558 | 7637.4504 | 8183.8819 | 8183.8819 | 11297.0036 | 17099.103 | 1.8 | 2202.5879 | 2837.3786 | 3411.713 | 4602.2362 | 8183.6584 | 12386.8508
1.9 | 81.673 | 85.3893 | 89.6113 | 96.4125 | 120.7734 | 159.2661 | 247.2493 | 504.6897 | 1.9 | 123.7907 | 126.8876 | 132.8916 | 139.0745 | 171.1805 | 220.671 | 326.0676 | 649.9561 | 681.0291 | 1.9 | 297.2164 | 304.0296 | 310.9591 | 325.7981 | 365.4768 | 439.7126 | 634.9254 | 1267.5324 | 1.9 | 40.5453 |  | 1.9 | 100.8737 |  | 1.9 | 6807.3395 | 7463.8324 | 8183.8819 | 8183.8819 | 10788.8216 | 16709.383 | 1.9 | 2152.9827 | 2773.0469 | 3411.713 | 4497.6004 | 7997.7144 | 12105.3117
2 | 81.673 | 85.3893 | 89.6113 | 96.4125 | 118.0239 | 159.2661 | 241.7504 | 493.0374 | 2 | 121.3132 | 123.7907 | 129.8002 | 139.0745 | 167.5145 | 220.671 | 326.0676 | 649.9561 | 665.4926 | 2 | 283.5901 | 290.4033 | 297.3567 | 304.1579 | 348.9799 | 429.6312 | 606.5142 | 1210.8241 | 2 | 39.6223 |  | 2 | 98.3962 |  | 2 | 6652.3234 | 7294.0898 | 7997.8627 | 8183.8819 | 10543.4923 | 16709.383 | 2 | 2103.3776 | 2710.2654 | 3334.205 | 4497.6004 | 7815.6645 | 11829.82
2.1 | 79.8149 | 83.5312 | 87.7564 | 93.9393 | 118.0239 | 155.6001 | 236.2514 | 482.1618 | 2.1 | 121.3132 | 123.7907 | 126.7087 | 135.9831 | 162.9321 | 215.1721 | 318.7357 | 635.1964 | 649.9561 | 2.1 | 271.2026 | 277.3963 | 283.7544 | 297.3567 | 333.3996 | 410.3849 | 592.7668 | 1182.8584 | 2.1 | 39.6223 |  | 2.1 | 95.9187 |  | 2.1 | 6652.3234 | 7294.0898 | 7997.8627 | 8183.8819 | 10303.0307 | 16329.07 | 2.1 | 2103.3776 | 2648.259 | 3334.205 | 4395.2898 | 7815.6645 | 11560.3756
2.2 | 79.8149 | 83.5312 | 85.9016 | 93.9393 | 115.2745 | 155.6001 | 236.2514 | 482.1618 | 2.2 | 118.2163 | 121.3132 | 123.6173 | 135.9831 | 162.9321 | 210.5896 | 311.4038 | 620.4367 | 649.9561 | 2.2 | 258.815 | 265.0088 | 270.7703 | 283.7544 | 326.0676 | 401.22 | 579.0194 | 1155.6695 | 2.2 | 39.6223 |  | 2.2 | 94.0606 |  | 2.2 | 6353.1425 | 7128.2227 | 7815.7188 | 8183.8819 | 10068.4102 | 15957.4922 | 2.2 | 2103.3776 | 2648.259 | 3258.2471 | 4395.2898 | 7637.5087 | 11560.3756
2.3 | 79.8149 | 81.673 | 85.9016 | 93.9393 | 115.2745 | 152.8506 | 230.7525 | 471.2862 | 2.3 | 115.7388 | 121.3132 | 123.6173 | 132.8916 | 159.2661 | 210.5896 | 311.4038 | 620.4367 | 635.1964 | 2.3 | 252.6212 | 258.815 | 264.5874 | 277.5715 | 318.7357 | 392.0551 | 553.3577 | 1130.0342 | 2.3 | 38.7204 |  | 2.3 | 94.0606 |  | 2.3 | 6208.2024 | 6807.3395 | 7463.8324 | 8183.8819 | 10068.4102 | 15957.4922 | 2.3 | 2056.0977 | 2587.8027 | 3183.8394 | 4295.3045 | 7464.2206 | 11560.3756
2.4 | 77.9568 | 81.673 | 85.9016 | 92.0845 | 112.525 | 149.1847 | 230.7525 | 471.2862 | 2.4 | 115.7388 | 118.2163 | 123.6173 | 132.8916 | 159.2661 | 206.0072 | 304.0718 | 606.4539 | 635.1964 | 2.4 | 241.4724 | 247.0468 | 252.8399 | 264.5874 | 311.4038 | 382.8901 | 540.5268 | 1103.6222 | 2.4 | 38.7204 |  | 2.4 | 94.0606 |  | 2.4 | 5929.1736 | 6501.1828 | 7128.2227 | 8183.8819 | 10068.4102 | 15957.4922 | 2.4 | 2056.0977 | 2528.8966 | 3183.8394 | 4295.3045 | 7464.2206 | 11296.9787
2.5 | 77.9568 | 79.8149 | 85.9016 | 92.0845 | 112.525 | 149.1847 | 225.2535 | 460.4107 | 2.5 | 115.7388 | 118.2163 | 121.1441 | 129.8002 | 155.6001 | 206.0072 | 304.0718 | 606.4539 | 620.4367 | 2.5 | 235.898 | 241.4724 | 247.2752 | 259.0228 | 304.0718 | 373.7252 | 540.5268 | 1078.7638 | 2.5 | 37.839 |  | 2.5 | 94.0606 |  | 2.5 | 5661.7709 | 6208.2024 | 6807.3395 | 8183.8819 | 10068.4102 | 15594.6494 | 2.5 | 2056.0977 | 2471.5407 | 3111.757 | 4197.6444 | 7464.2206 | 11296.9787
2.6 | 76.0986 | 79.8149 | 84.0467 | 89.6113 | 112.525 | 149.1847 | 225.2535 | 460.4107 | 2.6 | 113.2613 | 115.7388 | 121.1441 | 129.8002 | 155.6001 | 200.5082 | 296.7399 | 593.2478 | 620.4367 | 2.6 | 230.943 | 235.898 | 241.7106 | 252.8399 | 296.7399 | 365.4768 | 528.6124 | 1054.6822 | 2.6 | 37.839 |  | 2.6 | 91.5831 |  | 2.6 | 5406.7695 | 5929.1736 | 6652.3234 | 7997.8627 | 10068.4102 | 15239.1979 | 2.6 | 2056.0977 | 2471.5407 | 3111.757 | 4197.6444 | 7293.8531 | 11040.301
2.7 | 76.0986 | 79.8149 | 84.0467 | 89.6113 | 110.692 | 145.5187 | 225.2535 | 460.4107 | 2.7 | 110.1644 | 115.7388 | 121.1441 | 126.7087 | 152.8506 | 200.5082 | 296.7399 | 593.2478 | 606.4539 | 2.7 | 225.3686 | 230.943 | 236.146 | 247.2752 | 290.3244 | 357.2284 | 516.698 | 1030.6006 | 2.7 | 36.9777 |  | 2.7 | 91.5831 |  | 2.7 | 5284.3068 | 5793.5345 | 6353.1425 | 7815.7188 | 10068.4102 | 15239.1979 | 2.7 | 2056.0977 | 2414.9599 | 3040.4496 | 4197.6444 | 7293.8531 | 11040.301
2.8 | 74.8599 | 79.8149 | 81.5735 | 89.6113 | 110.692 | 145.5187 | 220.671 | 449.5351 | 2.8 | 110.1644 | 115.7388 | 118.0526 | 126.7087 | 152.8506 | 200.5082 | 296.7399 | 579.265 | 606.4539 | 2.8 | 220.4136 | 225.3686 | 230.5814 | 241.7106 | 283.909 | 357.2284 | 504.7836 | 1006.519 | 2.8 | 36.9777 |  | 2.8 | 89.725 |  | 2.8 | 5046.3572 | 5661.7709 | 6208.2024 | 7637.4504 | 10068.4102 | 14892.4815 | 2.8 | 2008.8178 | 2414.9599 | 3040.4496 | 4101.5344 | 7293.8531 | 10788.9988
2.9 | 74.8599 | 77.9568 | 81.5735 | 89.6113 | 110.692 | 145.5187 | 220.671 | 449.5351 | 2.9 | 110.1644 | 113.2613 | 118.0526 | 123.6173 | 149.1847 | 195.9258 | 290.3244 | 579.265 | 593.2478 | 2.9 | 215.4586 | 220.4136 | 225.6351 | 241.7106 | 277.4936 | 348.9799 | 504.7836 | 1006.519 | 2.9 | 36.9777 |  | 2.9 | 89.725 |  | 2.9 | 4931.6453 | 5406.7695 | 6067.1379 | 7637.4504 | 10068.4102 | 14553.8283 | 2.9 | 1963.0881 | 2359.9292 | 2971.4675 | 4101.5344 | 7128.3531 | 10788.9988
3 | 74.8599 | 77.9568 | 81.5735 | 87.7564 | 107.9425 | 145.5187 | 220.671 | 449.5351 | 3 | 110.1644 | 113.2613 | 115.5795 | 123.6173 | 149.1847 | 195.9258 | 290.3244 | 579.265 | 593.2478 | 3 | 210.5036 | 215.4586 | 220.0705 | 236.146 | 277.4936 | 348.9799 | 492.8692 | 983.9911 | 3 | 36.9777 |  | 3 | 89.725 |  | 3 | 4819.2587 | 5284.3068 | 5929.1736 | 7463.8324 | 10068.4102 | 14553.8283 | 3 | 1963.0881 | 2359.9292 | 2971.4675 | 4101.5344 | 7128.3531 | 10788.9988
3.1 | 74.8599 | 77.9568 | 79.7187 | 87.7564 | 107.9425 | 141.8527 | 220.671 | 439.4364 | 3.1 | 107.6869 | 113.2613 | 115.5795 | 123.6173 | 149.1847 | 192.2598 | 283.909 | 566.0589 | 593.2478 | 3.1 | 205.5486 | 210.5036 | 220.0705 | 230.5814 | 271.0781 | 340.7315 | 492.8692 | 961.4631 | 3.1 | 36.136 |  | 3.1 | 89.725 |  | 3.1 | 4602.2362 | 5164.1694 | 5793.5345 | 7294.0898 | 10068.4102 | 14222.5663 | 3.1 | 1918.9085 | 2306.4486 | 2904.0355 | 4008.5248 | 7128.3531 | 10543.0721
3.2 | 74.8599 | 76.0986 | 79.7187 | 87.7564 | 107.9425 | 141.8527 | 215.1721 | 439.4364 | 3.2 | 107.6869 | 110.1644 | 115.5795 | 123.6173 | 149.1847 | 192.2598 | 283.909 | 566.0589 | 579.265 | 3.2 | 205.5486 | 210.5036 | 215.1242 | 225.6351 | 271.0781 | 340.7315 | 481.8713 | 961.4631 | 3.2 | 36.136 |  | 3.2 | 89.725 |  | 3.2 | 4497.6004 | 5046.3572 | 5661.7709 | 7294.0898 | 10068.4102 | 14222.5663 | 3.2 | 1918.9085 | 2306.4486 | 2904.0355 | 4008.5248 | 6965.7738 | 10543.0721
3.3 | 74.8599 | 76.0986 | 79.7187 | 87.7564 | 107.9425 | 141.8527 | 215.1721 | 439.4364 | 3.3 | 105.2094 | 110.1644 | 115.5795 | 123.6173 | 145.5187 | 192.2598 | 283.909 | 566.0589 | 579.265 | 3.3 | 200.5935 | 205.5486 | 210.1779 | 225.6351 | 264.6627 | 333.3996 | 481.8713 | 939.712 | 3.3 | 36.136 |  | 3.3 | 87.8668 |  | 3.3 | 4295.3045 | 4819.2587 | 5533.1076 | 7128.2227 | 10068.4102 | 13898.6956 | 3.3 | 1874.7289 | 2253.7432 | 2837.3786 | 3917.0653 | 6965.7738 | 10543.0721
3.4 | 74.8599 | 76.0986 | 79.7187 | 85.9016 | 105.1931 | 141.8527 | 215.1721 | 439.4364 | 3.4 | 105.2094 | 110.1644 | 113.1063 | 121.1441 | 145.5187 | 192.2598 | 283.909 | 553.6297 | 579.265 | 3.4 | 196.2579 | 200.5935 | 210.1779 | 220.0705 | 259.1637 | 333.3996 | 470.8734 | 939.712 | 3.4 | 36.136 |  | 3.4 | 87.8668 |  | 3.4 | 4197.6444 | 4709.1973 | 5406.7695 | 6965.4558 | 10068.4102 | 13898.6956 | 3.4 | 1874.7289 | 2253.7432 | 2837.3786 | 3917.0653 | 6965.7738 | 10303.1927
3.5 | 74.8599 | 74.8599 | 79.7187 | 85.9016 | 105.1931 | 139.1033 | 215.1721 | 429.3377 | 3.5 | 105.2094 | 110.1644 | 113.1063 | 121.1441 | 145.5187 | 187.6773 | 277.4936 | 553.6297 | 579.265 | 3.5 | 191.9222 | 200.5935 | 205.8498 | 220.0705 | 259.1637 | 326.0676 | 470.8734 | 917.9609 | 3.5 | 35.3134 |  | 3.5 | 87.8668 |  | 3.5 | 4101.5344 | 4709.1973 | 5406.7695 | 6965.4558 | 10068.4102 | 13898.6956 | 3.5 | 1832.0995 | 2202.5879 | 2773.0469 | 3917.0653 | 6965.7738 | 10303.1927
3.6 | 73.0018 | 74.8599 | 79.7187 | 85.9016 | 105.1931 | 139.1033 | 210.5896 | 429.3377 | 3.6 | 105.2094 | 107.6869 | 113.1063 | 121.1441 | 145.5187 | 187.6773 | 277.4936 | 553.6297 | 566.0589 | 3.6 | 191.9222 | 196.2579 | 200.9035 | 215.1242 | 252.7483 | 326.0676 | 470.8734 | 917.9609 | 3.6 | 35.3134 |  | 3.6 | 85.3893 |  | 3.6 | 4008.5248 | 4602.2362 | 5284.3068 | 6807.3395 | 10068.4102 | 13898.6956 | 3.6 | 1832.0995 | 2202.5879 | 2773.0469 | 3827.9311 | 6965.7738 | 10303.1927
3.7 | 73.0018 | 74.8599 | 77.8638 | 85.9016 | 105.1931 | 139.1033 | 210.5896 | 429.3377 | 3.7 | 105.2094 | 107.6869 | 110.6332 | 121.1441 | 145.5187 | 187.6773 | 277.4936 | 553.6297 | 566.0589 | 3.7 | 187.5866 | 191.9222 | 200.9035 | 215.1242 | 252.7483 | 318.7357 | 459.8755 | 896.9866 | 3.7 | 35.3134 |  | 3.7 | 85.3893 |  | 3.7 | 3917.0653 | 4497.6004 | 5164.1694 | 6807.3395 | 10068.4102 | 13898.6956 | 3.7 | 1790.2452 | 2152.9827 | 2773.0469 | 3827.9311 | 6807.0886 | 10303.1927
3.8 | 73.0018 | 74.8599 | 77.8638 | 85.9016 | 105.1931 | 139.1033 | 210.5896 | 429.3377 | 3.8 | 102.7319 | 107.6869 | 110.6332 | 118.0526 | 141.8527 | 183.0949 | 277.4936 | 540.4237 | 566.0589 | 3.8 | 183.251 | 191.9222 | 196.5755 | 210.1779 | 252.7483 | 318.7357 | 459.8755 | 876.7891 | 3.8 | 35.3134 |  | 3.8 | 85.3893 |  | 3.8 | 3827.9311 | 4395.2898 | 5164.1694 | 6652.3234 | 10068.4102 | 13898.6956 | 3.8 | 1790.2452 | 2152.9827 | 2710.2654 | 3827.9311 | 6807.0886 | 10068.6888
3.9 | 73.0018 | 74.8599 | 77.8638 | 85.9016 | 105.1931 | 139.1033 | 210.5896 | 429.3377 | 3.9 | 102.7319 | 105.2094 | 110.6332 | 118.0526 | 141.8527 | 183.0949 | 271.0781 | 540.4237 | 566.0589 | 3.9 | 183.251 | 187.5866 | 196.5755 | 205.8498 | 247.2493 | 318.7357 | 449.7941 | 876.7891 | 3.9 | 35.3134 |  | 3.9 | 85.3893 |  | 3.9 | 3741.1221 | 4395.2898 | 5046.3572 | 6652.3234 | 9839.631 | 13582.2161 | 3.9 | 1790.2452 | 2152.9827 | 2710.2654 | 3741.1221 | 6807.0886 | 10068.6888
4 | 73.0018 | 74.8599 | 77.8638 | 85.9016 | 103.3601 | 139.1033 | 210.5896 | 429.3377 | 4 | 102.7319 | 105.2094 | 110.6332 | 118.0526 | 141.8527 | 183.0949 | 271.0781 | 540.4237 | 553.6297 | 4 | 178.9153 | 187.5866 | 191.6292 | 205.8498 | 247.2493 | 311.4038 | 449.7941 | 856.5917 | 4 | 34.5096 |  | 4 | 85.3893 |  | 4 | 3741.1221 | 4295.3045 | 5046.3572 | 6652.3234 | 9839.631 | 13582.2161 | 4 | 1749.941 | 2152.9827 | 2710.2654 | 3741.1221 | 6807.0886 | 10068.6888
4.1 | 71.1436 | 74.8599 | 77.8638 | 84.0467 | 103.3601 | 135.4373 | 210.5896 | 420.0158 | 4.1 | 100.8737 | 105.2094 | 110.6332 | 118.0526 | 139.1033 | 183.0949 | 271.0781 | 540.4237 | 553.6297 | 4.1 | 178.9153 | 183.251 | 191.6292 | 205.8498 | 241.7504 | 311.4038 | 439.7126 | 856.5917 | 4.1 | 34.5096 |  | 4.1 | 85.3893 |  | 4.1 | 3655.8633 | 4295.3045 | 4931.6453 | 6501.1828 | 9839.631 | 13582.2161 | 4.1 | 1749.941 | 2103.3776 | 2648.259 | 3741.1221 | 6807.0886 | 10068.6888
4.2 | 71.1436 | 74.8599 | 76.6272 | 84.0467 | 103.3601 | 135.4373 | 206.0072 | 420.0158 | 4.2 | 100.8737 | 105.2094 | 110.6332 | 115.5795 | 139.1033 | 183.0949 | 271.0781 | 540.4237 | 553.6297 | 4.2 | 175.1991 | 183.251 | 187.3011 | 200.9035 | 241.7504 | 304.0718 | 439.7126 | 837.171 | 4.2 | 34.5096 |  | 4.2 | 85.3893 |  | 4.2 | 3572.1546 | 4197.6444 | 4931.6453 | 6501.1828 | 9615.7193 | 13273.1278 | 4.2 | 1709.6369 | 2103.3776 | 2648.259 | 3741.1221 | 6652.2975 | 10068.6888
4.3 | 71.1436 | 74.8599 | 76.6272 | 84.0467 | 103.3601 | 135.4373 | 206.0072 | 420.0158 | 4.3 | 100.8737 | 105.2094 | 108.16 | 115.5795 | 139.1033 | 179.4289 | 271.0781 | 528.7713 | 553.6297 | 4.3 | 175.1991 | 178.9153 | 187.3011 | 200.9035 | 236.2514 | 304.0718 | 439.7126 | 837.171 | 4.3 | 34.5096 |  | 4.3 | 85.3893 |  | 4.3 | 3490.7712 | 4101.5344 | 4819.2587 | 6353.1425 | 9615.7193 | 13273.1278 | 4.3 | 1709.6369 | 2103.3776 | 2648.259 | 3655.8633 | 6652.2975 | 10068.6888
4.4 | 71.1436 | 74.8599 | 76.6272 | 84.0467 | 103.3601 | 135.4373 | 206.0072 | 420.0158 | 4.4 | 100.8737 | 105.2094 | 108.16 | 115.5795 | 139.1033 | 179.4289 | 264.6627 | 528.7713 | 553.6297 | 4.4 | 170.8634 | 178.9153 | 182.9731 | 196.5755 | 236.2514 | 304.0718 | 429.6312 | 837.171 | 4.4 | 34.5096 |  | 4.4 | 83.5312 |  | 4.4 | 3490.7712 | 4101.5344 | 4819.2587 | 6353.1425 | 9396.6753 | 13273.1278 | 4.4 | 1709.6369 | 2103.3776 | 2587.8027 | 3655.8633 | 6652.2975 | 10068.6888
4.5 | 71.1436 | 74.8599 | 76.6272 | 84.0467 | 103.3601 | 135.4373 | 206.0072 | 420.0158 | 4.5 | 100.8737 | 102.7319 | 108.16 | 115.5795 | 139.1033 | 179.4289 | 264.6627 | 528.7713 | 553.6297 | 4.5 | 170.8634 | 175.1991 | 182.9731 | 196.5755 | 236.2514 | 296.7399 | 429.6312 | 818.5272 | 4.5 | 34.5096 |  | 4.5 | 83.5312 |  | 4.5 | 3411.713 | 4008.5248 | 4819.2587 | 6353.1425 | 9396.6753 | 13273.1278 | 4.5 | 1670.8828 | 2103.3776 | 2587.8027 | 3655.8633 | 6652.2975 | 10068.6888
4.6 | 71.1436 | 74.8599 | 76.6272 | 84.0467 | 103.3601 | 135.4373 | 206.0072 | 420.0158 | 4.6 | 100.8737 | 102.7319 | 108.16 | 115.5795 | 139.1033 | 179.4289 | 264.6627 | 528.7713 | 553.6297 | 4.6 | 167.1471 | 175.1991 | 179.2634 | 191.6292 | 230.7525 | 296.7399 | 429.6312 | 818.5272 | 4.6 | 34.5096 |  | 4.6 | 83.5312 |  | 4.6 | 3334.205 | 4008.5248 | 4709.1973 | 6208.2024 | 9396.6753 | 13273.1278 | 4.6 | 1670.8828 | 2103.3776 | 2587.8027 | 3655.8633 | 6652.2975 | 10068.6888
4.7 | 69.9049 | 74.8599 | 76.6272 | 84.0467 | 103.3601 | 135.4373 | 206.0072 | 420.0158 | 4.7 | 100.8737 | 102.7319 | 105.6868 | 115.5795 | 139.1033 | 179.4289 | 264.6627 | 528.7713 | 540.4237 | 4.7 | 167.1471 | 170.8634 | 179.2634 | 191.6292 | 230.7525 | 296.7399 | 419.5498 | 818.5272 | 4.7 | 34.5096 |  | 4.7 | 83.5312 |  | 4.7 | 3334.205 | 4008.5248 | 4709.1973 | 6208.2024 | 9182.499 | 12970.7588 | 4.7 | 1670.8828 | 2103.3776 | 2587.8027 | 3655.8633 | 6652.2975 | 10068.6888
4.8 | 69.9049 | 74.8599 | 76.6272 | 84.0467 | 100.6106 | 135.4373 | 206.0072 | 420.0158 | 4.8 | 100.8737 | 102.7319 | 105.6868 | 115.5795 | 135.4373 | 179.4289 | 264.6627 | 528.7713 | 540.4237 | 4.8 | 163.4309 | 170.8634 | 174.9353 | 191.6292 | 225.2535 | 290.3244 | 419.5498 | 799.8834 | 4.8 | 34.5096 |  | 4.8 | 83.5312 |  | 4.8 | 3258.2471 | 3917.0653 | 4709.1973 | 6208.2024 | 9182.499 | 12970.7588 | 4.8 | 1632.9039 | 2103.3776 | 2587.8027 | 3572.1546 | 6500.4271 | 10068.6888
4.9 | 69.9049 | 74.8599 | 76.6272 | 81.5735 | 100.6106 | 135.4373 | 206.0072 | 420.0158 | 4.9 | 100.8737 | 102.7319 | 105.6868 | 115.5795 | 135.4373 | 179.4289 | 264.6627 | 528.7713 | 540.4237 | 4.9 | 163.4309 | 170.8634 | 174.9353 | 187.3011 | 225.2535 | 290.3244 | 419.5498 | 799.8834 | 4.9 | 34.5096 |  | 4.9 | 83.5312 |  | 4.9 | 3183.8394 | 3917.0653 | 4602.2362 | 6067.1379 | 9182.499 | 12970.7588 | 4.9 | 1632.9039 | 2103.3776 | 2528.8966 | 3572.1546 | 6500.4271 | 10068.6888
5 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 135.4373 | 206.0072 | 420.0158 | 5 | 98.3962 | 100.8737 | 105.6868 | 113.1063 | 135.4373 | 179.4289 | 264.6627 | 528.7713 | 540.4237 | 5 | 163.4309 | 167.1471 | 174.9353 | 187.3011 | 225.2535 | 290.3244 | 410.3849 | 799.8834 | 5 | 34.5096 |  | 5 | 83.5312 |  | 5 | 3183.8394 | 3827.9311 | 4602.2362 | 6067.1379 | 9182.499 | 12970.7588 | 5 | 1632.9039 | 2103.3776 | 2528.8966 | 3572.1546 | 6500.4271 | 10068.6888
5.1 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 135.4373 | 206.0072 | 420.0158 | 5.1 | 98.3962 | 100.8737 | 105.6868 | 113.1063 | 135.4373 | 174.8464 | 264.6627 | 516.3421 | 540.4237 | 5.1 | 159.7146 | 167.1471 | 171.2256 | 182.9731 | 220.671 | 283.909 | 410.3849 | 781.2396 | 5.1 | 34.5096 |  | 5.1 | 81.673 |  | 5.1 | 3111.757 | 3827.9311 | 4602.2362 | 6067.1379 | 8973.1903 | 12970.7588 | 5.1 | 1632.9039 | 2103.3776 | 2528.8966 | 3572.1546 | 6500.4271 | 10068.6888
5.2 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 135.4373 | 206.0072 | 409.917 | 5.2 | 98.3962 | 100.8737 | 105.6868 | 113.1063 | 135.4373 | 174.8464 | 259.1637 | 516.3421 | 540.4237 | 5.2 | 159.7146 | 163.4309 | 171.2256 | 182.9731 | 220.671 | 283.909 | 410.3849 | 781.2396 | 5.2 | 34.5096 |  | 5.2 | 81.673 |  | 5.2 | 3111.757 | 3741.1221 | 4497.6004 | 5929.1736 | 8973.1903 | 12970.7588 | 5.2 | 1595.7001 | 2103.3776 | 2528.8966 | 3572.1546 | 6500.4271 | 10068.6888
5.3 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 135.4373 | 206.0072 | 409.917 | 5.3 | 98.3962 | 100.8737 | 105.6868 | 113.1063 | 135.4373 | 174.8464 | 259.1637 | 516.3421 | 540.4237 | 5.3 | 159.7146 | 163.4309 | 171.2256 | 182.9731 | 220.671 | 283.909 | 401.22 | 781.2396 | 5.3 | 34.5096 |  | 5.3 | 81.673 |  | 5.3 | 3040.4496 | 3741.1221 | 4497.6004 | 5929.1736 | 8973.1903 | 12675.7811 | 5.3 | 1595.7001 | 2103.3776 | 2528.8966 | 3572.1546 | 6500.4271 | 10068.6888
5.4 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 5.4 | 98.3962 | 100.8737 | 105.6868 | 113.1063 | 135.4373 | 174.8464 | 259.1637 | 516.3421 | 540.4237 | 5.4 | 155.9983 | 163.4309 | 166.8976 | 179.2634 | 215.1721 | 277.4936 | 401.22 | 764.1494 | 5.4 | 34.5096 |  | 5.4 | 81.673 |  | 5.4 | 3040.4496 | 3741.1221 | 4497.6004 | 5929.1736 | 8769.7228 | 12675.7811 | 5.4 | 1595.7001 | 2103.3776 | 2471.5407 | 3572.1546 | 6500.4271 | 10068.6888
5.5 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 5.5 | 95.9187 | 100.8737 | 105.6868 | 113.1063 | 135.4373 | 174.8464 | 259.1637 | 516.3421 | 540.4237 | 5.5 | 155.9983 | 159.7146 | 166.8976 | 179.2634 | 215.1721 | 277.4936 | 401.22 | 764.1494 | 5.5 | 34.5096 |  | 5.5 | 81.673 |  | 5.5 | 2971.4675 | 3655.8633 | 4395.2898 | 5929.1736 | 8769.7228 | 12675.7811 | 5.5 | 1595.7001 | 2103.3776 | 2471.5407 | 3490.7712 | 6500.4271 | 10068.6888
5.6 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 5.6 | 95.9187 | 100.8737 | 103.2137 | 110.6332 | 135.4373 | 174.8464 | 259.1637 | 516.3421 | 528.7713 | 5.6 | 155.9983 | 159.7146 | 163.1878 | 179.2634 | 215.1721 | 277.4936 | 392.0551 | 764.1494 | 5.6 | 34.5096 |  | 5.6 | 81.673 |  | 5.6 | 2971.4675 | 3655.8633 | 4395.2898 | 5793.5345 | 8769.7228 | 12675.7811 | 5.6 | 1559.2713 | 2056.0977 | 2471.5407 | 3490.7712 | 6352.4507 | 10068.6888
5.7 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 5.7 | 95.9187 | 100.8737 | 103.2137 | 110.6332 | 135.4373 | 174.8464 | 259.1637 | 516.3421 | 528.7713 | 5.7 | 152.2821 | 159.7146 | 163.1878 | 174.9353 | 215.1721 | 277.4936 | 392.0551 | 746.2825 | 5.7 | 34.5096 |  | 5.7 | 81.673 |  | 5.7 | 2971.4675 | 3572.1546 | 4395.2898 | 5793.5345 | 8570.1494 | 12675.7811 | 5.7 | 1559.2713 | 2056.0977 | 2471.5407 | 3490.7712 | 6352.4507 | 10068.6888
5.8 | 69.9049 | 73.0018 | 74.7723 | 81.5735 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 5.8 | 95.9187 | 100.8737 | 103.2137 | 110.6332 | 132.6878 | 174.8464 | 259.1637 | 516.3421 | 528.7713 | 5.8 | 152.2821 | 155.9983 | 163.1878 | 174.9353 | 210.5896 | 271.0781 | 392.0551 | 746.2825 | 5.8 | 34.5096 |  | 5.8 | 81.673 |  | 5.8 | 2904.0355 | 3572.1546 | 4395.2898 | 5793.5345 | 8570.1494 | 12675.7811 | 5.8 | 1559.2713 | 2056.0977 | 2471.5407 | 3490.7712 | 6352.4507 | 10068.6888
5.9 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 5.9 | 95.9187 | 100.8737 | 103.2137 | 110.6332 | 132.6878 | 174.8464 | 259.1637 | 516.3421 | 528.7713 | 5.9 | 149.1852 | 155.9983 | 159.4781 | 174.9353 | 210.5896 | 271.0781 | 392.0551 | 746.2825 | 5.9 | 34.5096 |  | 5.9 | 79.8149 |  | 5.9 | 2904.0355 | 3572.1546 | 4295.3045 | 5793.5345 | 8570.1494 | 12386.8508 | 5.9 | 1559.2713 | 2056.0977 | 2471.5407 | 3490.7712 | 6352.4507 | 10068.6888
6 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 6 | 94.0606 | 100.8737 | 103.2137 | 110.6332 | 132.6878 | 171.1805 | 259.1637 | 504.6897 | 528.7713 | 6 | 149.1852 | 155.9983 | 159.4781 | 171.2256 | 210.5896 | 271.0781 | 382.8901 | 729.1923 | 6 | 34.5096 |  | 6 | 79.8149 |  | 6 | 2904.0355 | 3490.7712 | 4295.3045 | 5661.7709 | 8570.1494 | 12386.8508 | 6 | 1523.6176 | 2056.0977 | 2414.9599 | 3490.7712 | 6352.4507 | 10068.6888
6.1 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 6.1 | 94.0606 | 98.3962 | 103.2137 | 110.6332 | 132.6878 | 171.1805 | 259.1637 | 504.6897 | 528.7713 | 6.1 | 149.1852 | 152.2821 | 159.4781 | 171.2256 | 206.0072 | 271.0781 | 382.8901 | 729.1923 | 6.1 | 34.5096 |  | 6.1 | 79.8149 |  | 6.1 | 2837.3786 | 3490.7712 | 4295.3045 | 5661.7709 | 8374.4701 | 12386.8508 | 6.1 | 1523.6176 | 2056.0977 | 2414.9599 | 3490.7712 | 6352.4507 | 10068.6888
6.2 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 6.2 | 94.0606 | 98.3962 | 100.7405 | 110.6332 | 132.6878 | 171.1805 | 252.7483 | 504.6897 | 528.7713 | 6.2 | 149.1852 | 152.2821 | 159.4781 | 171.2256 | 206.0072 | 264.6627 | 382.8901 | 729.1923 | 6.2 | 34.5096 |  | 6.2 | 79.8149 |  | 6.2 | 2837.3786 | 3490.7712 | 4197.6444 | 5661.7709 | 8374.4701 | 12386.8508 | 6.2 | 1523.6176 | 2008.8178 | 2414.9599 | 3411.713 | 6352.4507 | 10068.6888
6.3 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 6.3 | 94.0606 | 98.3962 | 100.7405 | 110.6332 | 132.6878 | 171.1805 | 252.7483 | 504.6897 | 528.7713 | 6.3 | 145.4689 | 152.2821 | 155.7683 | 166.8976 | 206.0072 | 264.6627 | 382.8901 | 729.1923 | 6.3 | 33.7241 |  | 6.3 | 79.8149 |  | 6.3 | 2837.3786 | 3411.713 | 4197.6444 | 5661.7709 | 8374.4701 | 12386.8508 | 6.3 | 1523.6176 | 2008.8178 | 2414.9599 | 3411.713 | 6352.4507 | 10068.6888
6.4 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 6.4 | 94.0606 | 98.3962 | 100.7405 | 110.6332 | 132.6878 | 171.1805 | 252.7483 | 504.6897 | 528.7713 | 6.4 | 145.4689 | 149.1852 | 155.7683 | 166.8976 | 206.0072 | 264.6627 | 373.7252 | 712.879 | 6.4 | 33.7241 |  | 6.4 | 79.8149 |  | 6.4 | 2773.0469 | 3411.713 | 4197.6444 | 5533.1076 | 8374.4701 | 12386.8508 | 6.4 | 1523.6176 | 2008.8178 | 2414.9599 | 3411.713 | 6352.4507 | 10068.6888
6.5 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 6.5 | 94.0606 | 98.3962 | 100.7405 | 110.6332 | 129.9383 | 171.1805 | 252.7483 | 504.6897 | 528.7713 | 6.5 | 145.4689 | 149.1852 | 155.7683 | 166.8976 | 200.5082 | 259.1637 | 373.7252 | 712.879 | 6.5 | 33.7241 |  | 6.5 | 79.8149 |  | 6.5 | 2773.0469 | 3411.713 | 4197.6444 | 5533.1076 | 8374.4701 | 12386.8508 | 6.5 | 1489.5141 | 2008.8178 | 2414.9599 | 3411.713 | 6208.3684 | 10068.6888
6.6 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 409.917 | 6.6 | 94.0606 | 98.3962 | 100.7405 | 108.16 | 129.9383 | 171.1805 | 252.7483 | 504.6897 | 516.3421 | 6.6 | 145.4689 | 149.1852 | 155.7683 | 163.1878 | 200.5082 | 259.1637 | 373.7252 | 712.879 | 6.6 | 33.7241 |  | 6.6 | 79.8149 |  | 6.6 | 2773.0469 | 3411.713 | 4101.5344 | 5533.1076 | 8374.4701 | 12105.3117 | 6.6 | 1489.5141 | 2008.8178 | 2359.9292 | 3411.713 | 6208.3684 | 10068.6888
6.7 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 400.5951 | 6.7 | 94.0606 | 95.9187 | 100.7405 | 108.16 | 129.9383 | 171.1805 | 252.7483 | 504.6897 | 516.3421 | 6.7 | 145.4689 | 149.1852 | 152.6769 | 163.1878 | 200.5082 | 259.1637 | 373.7252 | 712.879 | 6.7 | 33.7241 |  | 6.7 | 79.8149 |  | 6.7 | 2710.2654 | 3334.205 | 4101.5344 | 5533.1076 | 8374.4701 | 12105.3117 | 6.7 | 1489.5141 | 1963.0881 | 2359.9292 | 3411.713 | 6208.3684 | 10068.6888
6.8 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 100.6106 | 132.6878 | 200.5082 | 400.5951 | 6.8 | 94.0606 | 95.9187 | 100.7405 | 108.16 | 129.9383 | 171.1805 | 252.7483 | 504.6897 | 516.3421 | 6.8 | 142.372 | 149.1852 | 152.6769 | 163.1878 | 200.5082 | 259.1637 | 365.4768 | 696.5656 | 6.8 | 33.7241 |  | 6.8 | 79.8149 |  | 6.8 | 2710.2654 | 3334.205 | 4101.5344 | 5406.7695 | 8374.4701 | 12105.3117 | 6.8 | 1489.5141 | 1963.0881 | 2359.9292 | 3411.713 | 6208.3684 | 10068.6888
6.9 | 69.9049 | 71.1436 | 74.7723 | 79.7187 | 98.7776 | 129.9383 | 200.5082 | 400.5951 | 6.9 | 94.0606 | 95.9187 | 100.7405 | 108.16 | 129.9383 | 171.1805 | 252.7483 | 504.6897 | 516.3421 | 6.9 | 142.372 | 145.4689 | 152.6769 | 163.1878 | 195.9258 | 252.7483 | 365.4768 | 696.5656 | 6.9 | 33.7241 |  | 6.9 | 79.8149 |  | 6.9 | 2710.2654 | 3334.205 | 4008.5248 | 5406.7695 | 8374.4701 | 12105.3117 | 6.9 | 1489.5141 | 1963.0881 | 2359.9292 | 3334.205 | 6208.3684 | 10068.6888
7 | 69.9049 | 69.9049 | 74.7723 | 79.7187 | 98.7776 | 129.9383 | 200.5082 | 400.5951 | 7 | 94.0606 | 95.9187 | 100.7405 | 108.16 | 129.9383 | 171.1805 | 252.7483 | 504.6897 | 516.3421 | 7 | 142.372 | 145.4689 | 148.9671 | 163.1878 | 195.9258 | 252.7483 | 365.4768 | 696.5656 | 7 | 33.7241 |  | 7 | 79.8149 |  | 7 | 2710.2654 | 3334.205 | 4008.5248 | 5406.7695 | 8374.4701 | 12105.3117 | 7 | 1489.5141 | 1963.0881 | 2359.9292 | 3334.205 | 6208.3684 | 10068.6888
7.1 | 69.9049 | 69.9049 | 74.7723 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.1 | 94.0606 | 95.9187 | 100.7405 | 108.16 | 129.9383 | 171.1805 | 252.7483 | 504.6897 | 516.3421 | 7.1 | 139.2752 | 145.4689 | 148.9671 | 159.4781 | 195.9258 | 252.7483 | 365.4768 | 696.5656 | 7.1 | 33.7241 |  | 7.1 | 79.8149 |  | 7.1 | 2648.259 | 3258.2471 | 4008.5248 | 5406.7695 | 8374.4701 | 12105.3117 | 7.1 | 1455.4105 | 1963.0881 | 2359.9292 | 3334.205 | 6208.3684 | 10068.6888
7.2 | 68.0467 | 69.9049 | 74.7723 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.2 | 94.0606 | 95.9187 | 100.7405 | 108.16 | 129.9383 | 167.5145 | 252.7483 | 493.0374 | 516.3421 | 7.2 | 139.2752 | 145.4689 | 148.9671 | 159.4781 | 195.9258 | 252.7483 | 357.2284 | 681.0291 | 7.2 | 33.7241 |  | 7.2 | 79.8149 |  | 7.2 | 2648.259 | 3258.2471 | 3917.0653 | 5284.3068 | 8374.4701 | 12105.3117 | 7.2 | 1455.4105 | 1963.0881 | 2359.9292 | 3334.205 | 6208.3684 | 10068.6888
7.3 | 68.0467 | 69.9049 | 74.7723 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.3 | 91.5831 | 95.9187 | 100.7405 | 108.16 | 129.9383 | 167.5145 | 252.7483 | 493.0374 | 516.3421 | 7.3 | 139.2752 | 145.4689 | 148.9671 | 159.4781 | 192.2598 | 252.7483 | 357.2284 | 681.0291 | 7.3 | 33.7241 |  | 7.3 | 79.8149 |  | 7.3 | 2648.259 | 3258.2471 | 3917.0653 | 5284.3068 | 8374.4701 | 12105.3117 | 7.3 | 1455.4105 | 1918.9085 | 2359.9292 | 3334.205 | 6208.3684 | 10068.6888
7.4 | 68.0467 | 69.9049 | 74.7723 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.4 | 91.5831 | 94.0606 | 100.7405 | 105.6868 | 129.9383 | 167.5145 | 252.7483 | 493.0374 | 516.3421 | 7.4 | 139.2752 | 142.372 | 148.9671 | 159.4781 | 192.2598 | 247.2493 | 357.2284 | 681.0291 | 7.4 | 33.7241 |  | 7.4 | 79.8149 |  | 7.4 | 2648.259 | 3258.2471 | 3917.0653 | 5284.3068 | 8374.4701 | 12105.3117 | 7.4 | 1455.4105 | 1918.9085 | 2306.4486 | 3334.205 | 6208.3684 | 10068.6888
7.5 | 68.0467 | 69.9049 | 74.7723 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.5 | 91.5831 | 94.0606 | 100.7405 | 105.6868 | 129.9383 | 167.5145 | 247.2493 | 493.0374 | 516.3421 | 7.5 | 139.2752 | 142.372 | 145.2574 | 155.7683 | 192.2598 | 247.2493 | 357.2284 | 681.0291 | 7.5 | 33.7241 |  | 7.5 | 79.8149 |  | 7.5 | 2648.259 | 3258.2471 | 3917.0653 | 5284.3068 | 8374.4701 | 11829.82 | 7.5 | 1455.4105 | 1918.9085 | 2306.4486 | 3334.205 | 6067.2067 | 10068.6888
7.6 | 68.0467 | 69.9049 | 74.7723 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.6 | 91.5831 | 94.0606 | 98.2674 | 105.6868 | 129.9383 | 167.5145 | 247.2493 | 493.0374 | 516.3421 | 7.6 | 139.2752 | 142.372 | 145.2574 | 155.7683 | 192.2598 | 247.2493 | 348.9799 | 681.0291 | 7.6 | 33.7241 |  | 7.6 | 77.9568 |  | 7.6 | 2587.8027 | 3183.8394 | 3917.0653 | 5284.3068 | 8374.4701 | 11829.82 | 7.6 | 1422.0821 | 1918.9085 | 2306.4486 | 3334.205 | 6067.2067 | 10068.6888
7.7 | 68.0467 | 69.9049 | 72.9175 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.7 | 91.5831 | 94.0606 | 98.2674 | 105.6868 | 129.9383 | 167.5145 | 247.2493 | 493.0374 | 516.3421 | 7.7 | 135.5589 | 142.372 | 145.2574 | 155.7683 | 187.6773 | 247.2493 | 348.9799 | 665.4926 | 7.7 | 33.7241 |  | 7.7 | 77.9568 |  | 7.7 | 2587.8027 | 3183.8394 | 3827.9311 | 5164.1694 | 8374.4701 | 11829.82 | 7.7 | 1422.0821 | 1918.9085 | 2306.4486 | 3334.205 | 6067.2067 | 10068.6888
7.8 | 68.0467 | 69.9049 | 72.9175 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.8 | 91.5831 | 94.0606 | 98.2674 | 105.6868 | 127.1889 | 167.5145 | 247.2493 | 493.0374 | 516.3421 | 7.8 | 135.5589 | 139.2752 | 145.2574 | 155.7683 | 187.6773 | 241.7504 | 348.9799 | 665.4926 | 7.8 | 33.7241 |  | 7.8 | 77.9568 |  | 7.8 | 2587.8027 | 3183.8394 | 3827.9311 | 5164.1694 | 8374.4701 | 11829.82 | 7.8 | 1422.0821 | 1918.9085 | 2306.4486 | 3258.2471 | 6067.2067 | 10068.6888
7.9 | 68.0467 | 69.9049 | 72.9175 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 400.5951 | 7.9 | 91.5831 | 94.0606 | 98.2674 | 105.6868 | 127.1889 | 167.5145 | 247.2493 | 493.0374 | 504.6897 | 7.9 | 135.5589 | 139.2752 | 145.2574 | 155.7683 | 187.6773 | 241.7504 | 348.9799 | 665.4926 | 7.9 | 33.7241 |  | 7.9 | 77.9568 |  | 7.9 | 2587.8027 | 3183.8394 | 3827.9311 | 5164.1694 | 8374.4701 | 11829.82 | 7.9 | 1422.0821 | 1918.9085 | 2306.4486 | 3258.2471 | 6067.2067 | 10068.6888
8 | 68.0467 | 69.9049 | 72.9175 | 79.7187 | 98.7776 | 129.9383 | 195.9258 | 392.05 | 8 | 91.5831 | 94.0606 | 98.2674 | 105.6868 | 127.1889 | 167.5145 | 247.2493 | 493.0374 | 504.6897 | 8 | 135.5589 | 139.2752 | 145.2574 | 152.6769 | 187.6773 | 241.7504 | 348.9799 | 665.4926 | 8 | 33.7241 |  | 8 | 77.9568 |  | 8 | 2587.8027 | 3183.8394 | 3827.9311 | 5164.1694 | 8374.4701 | 11829.82 | 8 | 1422.0821 | 1874.7289 | 2306.4486 | 3258.2471 | 6067.2067 | 10068.6888
8.1 | 68.0467 | 69.9049 | 72.9175 | 77.8638 | 98.7776 | 129.9383 | 195.9258 | 392.05 | 8.1 | 89.725 | 94.0606 | 98.2674 | 105.6868 | 127.1889 | 167.5145 | 247.2493 | 493.0374 | 504.6897 | 8.1 | 135.5589 | 139.2752 | 145.2574 | 152.6769 | 183.0949 | 241.7504 | 340.7315 | 665.4926 | 8.1 | 33.7241 |  | 8.1 | 77.9568 |  | 8.1 | 2528.8966 | 3111.757 | 3827.9311 | 5046.3572 | 8374.4701 | 11829.82 | 8.1 | 1422.0821 | 1874.7289 | 2306.4486 | 3258.2471 | 6067.2067 | 10068.6888
8.2 | 68.0467 | 69.9049 | 72.9175 | 77.8638 | 98.7776 | 129.9383 | 195.9258 | 392.05 | 8.2 | 89.725 | 94.0606 | 98.2674 | 105.6868 | 127.1889 | 167.5145 | 247.2493 | 493.0374 | 504.6897 | 8.2 | 135.5589 | 139.2752 | 142.166 | 152.6769 | 183.0949 | 241.7504 | 340.7315 | 665.4926 | 8.2 | 33.7241 |  | 8.2 | 77.9568 |  | 8.2 | 2528.8966 | 3111.757 | 3741.1221 | 5046.3572 | 8374.4701 | 11829.82 | 8.2 | 1422.0821 | 1874.7289 | 2306.4486 | 3258.2471 | 6067.2067 | 9839.5603
8.3 | 68.0467 | 69.9049 | 72.9175 | 77.8638 | 98.7776 | 129.9383 | 195.9258 | 392.05 | 8.3 | 89.725 | 94.0606 | 98.2674 | 105.6868 | 127.1889 | 162.9321 | 247.2493 | 493.0374 | 504.6897 | 8.3 | 132.462 | 139.2752 | 142.166 | 152.6769 | 183.0949 | 236.2514 | 340.7315 | 665.4926 | 8.3 | 33.7241 |  | 8.3 | 77.9568 |  | 8.3 | 2528.8966 | 3111.757 | 3741.1221 | 5046.3572 | 8374.4701 | 11829.82 | 8.3 | 1389.5287 | 1874.7289 | 2253.7432 | 3258.2471 | 6067.2067 | 9839.5603
8.4 | 66.808 | 69.9049 | 72.9175 | 77.8638 | 96.0281 | 129.9383 | 195.9258 | 392.05 | 8.4 | 89.725 | 94.0606 | 96.4125 | 105.6868 | 127.1889 | 162.9321 | 247.2493 | 493.0374 | 504.6897 | 8.4 | 132.462 | 135.5589 | 142.166 | 148.9671 | 183.0949 | 236.2514 | 340.7315 | 649.9561 | 8.4 | 33.7241 |  | 8.4 | 77.9568 |  | 8.4 | 2528.8966 | 3111.757 | 3741.1221 | 5046.3572 | 8374.4701 | 11829.82 | 8.4 | 1389.5287 | 1874.7289 | 2253.7432 | 3258.2471 | 6067.2067 | 9839.5603
8.5 | 66.808 | 69.9049 | 72.9175 | 77.8638 | 96.0281 | 129.9383 | 195.9258 | 392.05 | 8.5 | 89.725 | 94.0606 | 96.4125 | 105.6868 | 127.1889 | 162.9321 | 247.2493 | 493.0374 | 504.6897 | 8.5 | 132.462 | 135.5589 | 142.166 | 148.9671 | 183.0949 | 236.2514 | 340.7315 | 649.9561 | 8.5 | 33.7241 |  | 8.5 | 77.9568 |  | 8.5 | 2528.8966 | 3111.757 | 3741.1221 | 5046.3572 | 8374.4701 | 11829.82 | 8.5 | 1389.5287 | 1874.7289 | 2253.7432 | 3258.2471 | 6067.2067 | 9839.5603
8.6 | 66.808 | 69.9049 | 72.9175 | 77.8638 | 96.0281 | 129.9383 | 195.9258 | 392.05 | 8.6 | 89.725 | 94.0606 | 96.4125 | 105.6868 | 127.1889 | 162.9321 | 247.2493 | 482.1618 | 504.6897 | 8.6 | 132.462 | 135.5589 | 139.0745 | 148.9671 | 179.4289 | 236.2514 | 340.7315 | 649.9561 | 8.6 | 33.7241 |  | 8.6 | 77.9568 |  | 8.6 | 2528.8966 | 3040.4496 | 3741.1221 | 4931.6453 | 8374.4701 | 11560.3756 | 8.6 | 1389.5287 | 1874.7289 | 2253.7432 | 3258.2471 | 6067.2067 | 9839.5603
8.7 | 66.808 | 69.9049 | 72.9175 | 77.8638 | 96.0281 | 129.9383 | 195.9258 | 392.05 | 8.7 | 89.725 | 94.0606 | 96.4125 | 103.2137 | 127.1889 | 162.9321 | 247.2493 | 482.1618 | 504.6897 | 8.7 | 129.9845 | 135.5589 | 139.0745 | 148.9671 | 179.4289 | 236.2514 | 340.7315 | 649.9561 | 8.7 | 33.7241 |  | 8.7 | 76.0986 |  | 8.7 | 2471.5407 | 3040.4496 | 3741.1221 | 4931.6453 | 8374.4701 | 11560.3756 | 8.7 | 1389.5287 | 1832.0995 | 2253.7432 | 3258.2471 | 5928.9656 | 9839.5603
8.8 | 66.808 | 69.9049 | 72.9175 | 77.8638 | 96.0281 | 129.9383 | 195.9258 | 392.05 | 8.8 | 89.725 | 94.0606 | 96.4125 | 103.2137 | 123.5229 | 162.9321 | 247.2493 | 482.1618 | 504.6897 | 8.8 | 129.9845 | 135.5589 | 139.0745 | 148.9671 | 179.4289 | 230.7525 | 333.3996 | 649.9561 | 8.8 | 32.9564 |  | 8.8 | 76.0986 |  | 8.8 | 2471.5407 | 3040.4496 | 3655.8633 | 4931.6453 | 8374.4701 | 11560.3756 | 8.8 | 1389.5287 | 1832.0995 | 2253.7432 | 3183.8394 | 5928.9656 | 9839.5603
8.9 | 66.808 | 69.9049 | 72.9175 | 77.8638 | 96.0281 | 129.9383 | 195.9258 | 392.05 | 8.9 | 89.725 | 94.0606 | 96.4125 | 103.2137 | 123.5229 | 162.9321 | 247.2493 | 482.1618 | 504.6897 | 8.9 | 129.9845 | 135.5589 | 139.0745 | 148.9671 | 179.4289 | 230.7525 | 333.3996 | 649.9561 | 8.9 | 32.9564 |  | 8.9 | 76.0986 |  | 8.9 | 2471.5407 | 3040.4496 | 3655.8633 | 4931.6453 | 8374.4701 | 11560.3756 | 8.9 | 1389.5287 | 1832.0995 | 2253.7432 | 3183.8394 | 5928.9656 | 9839.5603
9 | 66.808 | 69.9049 | 71.0626 | 77.8638 | 96.0281 | 129.9383 | 195.9258 | 392.05 | 9 | 89.725 | 91.5831 | 96.4125 | 103.2137 | 123.5229 | 162.9321 | 241.7504 | 482.1618 | 504.6897 | 9 | 129.9845 | 135.5589 | 139.0745 | 148.9671 | 179.4289 | 230.7525 | 333.3996 | 649.9561 | 9 | 32.9564 |  | 9 | 76.0986 |  | 9 | 2471.5407 | 3040.4496 | 3655.8633 | 4819.2587 | 8183.6584 | 11560.3756 | 9 | 1358.5255 | 1832.0995 | 2253.7432 | 3183.8394 | 5928.9656 | 9839.5603
9.1 | 66.808 | 69.9049 | 71.0626 | 77.8638 | 96.0281 | 129.9383 | 195.9258 | 392.05 | 9.1 | 89.725 | 91.5831 | 96.4125 | 103.2137 | 123.5229 | 162.9321 | 241.7504 | 482.1618 | 504.6897 | 9.1 | 129.9845 | 132.462 | 139.0745 | 145.2574 | 179.4289 | 230.7525 | 333.3996 | 649.9561 | 9.1 | 32.9564 |  | 9.1 | 76.0986 |  | 9.1 | 2471.5407 | 3040.4496 | 3655.8633 | 4819.2587 | 8183.6584 | 11560.3756 | 9.1 | 1358.5255 | 1832.0995 | 2253.7432 | 3183.8394 | 5928.9656 | 9839.5603
9.2 | 66.808 | 69.9049 | 71.0626 | 77.8638 | 96.0281 | 129.9383 | 192.2598 | 392.05 | 9.2 | 89.725 | 91.5831 | 96.4125 | 103.2137 | 123.5229 | 162.9321 | 241.7504 | 482.1618 | 504.6897 | 9.2 | 129.9845 | 132.462 | 139.0745 | 145.2574 | 174.8464 | 230.7525 | 333.3996 | 635.1964 | 9.2 | 32.9564 |  | 9.2 | 76.0986 |  | 9.2 | 2471.5407 | 3040.4496 | 3655.8633 | 4819.2587 | 8183.6584 | 11560.3756 | 9.2 | 1358.5255 | 1832.0995 | 2253.7432 | 3183.8394 | 5928.9656 | 9839.5603
9.3 | 66.808 | 69.9049 | 71.0626 | 77.8638 | 96.0281 | 127.1889 | 192.2598 | 392.05 | 9.3 | 89.725 | 91.5831 | 93.9393 | 103.2137 | 123.5229 | 162.9321 | 241.7504 | 482.1618 | 504.6897 | 9.3 | 129.9845 | 132.462 | 135.9831 | 145.2574 | 174.8464 | 225.2535 | 333.3996 | 635.1964 | 9.3 | 32.9564 |  | 9.3 | 76.0986 |  | 9.3 | 2414.9599 | 2971.4675 | 3572.1546 | 4819.2587 | 8183.6584 | 11560.3756 | 9.3 | 1358.5255 | 1832.0995 | 2202.5879 | 3183.8394 | 5928.9656 | 9839.5603
9.4 | 66.808 | 69.9049 | 71.0626 | 77.8638 | 96.0281 | 127.1889 | 192.2598 | 392.05 | 9.4 | 89.725 | 91.5831 | 93.9393 | 103.2137 | 123.5229 | 162.9321 | 241.7504 | 482.1618 | 504.6897 | 9.4 | 129.9845 | 132.462 | 135.9831 | 145.2574 | 174.8464 | 225.2535 | 333.3996 | 635.1964 | 9.4 | 32.9564 |  | 9.4 | 76.0986 |  | 9.4 | 2414.9599 | 2971.4675 | 3572.1546 | 4819.2587 | 8183.6584 | 11560.3756 | 9.4 | 1358.5255 | 1832.0995 | 2202.5879 | 3183.8394 | 5928.9656 | 9839.5603
9.5 | 66.808 | 69.9049 | 71.0626 | 77.8638 | 96.0281 | 127.1889 | 192.2598 | 392.05 | 9.5 | 89.725 | 91.5831 | 93.9393 | 103.2137 | 123.5229 | 162.9321 | 241.7504 | 482.1618 | 493.0374 | 9.5 | 126.8876 | 132.462 | 135.9831 | 145.2574 | 174.8464 | 225.2535 | 326.0676 | 635.1964 | 9.5 | 32.9564 |  | 9.5 | 76.0986 |  | 9.5 | 2414.9599 | 2971.4675 | 3572.1546 | 4819.2587 | 8183.6584 | 11560.3756 | 9.5 | 1358.5255 | 1832.0995 | 2202.5879 | 3183.8394 | 5928.9656 | 9839.5603
9.6 | 66.808 | 69.9049 | 71.0626 | 76.6272 | 96.0281 | 127.1889 | 192.2598 | 392.05 | 9.6 | 89.725 | 91.5831 | 93.9393 | 103.2137 | 123.5229 | 162.9321 | 241.7504 | 482.1618 | 493.0374 | 9.6 | 126.8876 | 129.9845 | 135.9831 | 145.2574 | 174.8464 | 225.2535 | 326.0676 | 635.1964 | 9.6 | 32.9564 |  | 9.6 | 76.0986 |  | 9.6 | 2414.9599 | 2971.4675 | 3572.1546 | 4709.1973 | 7997.7144 | 11560.3756 | 9.6 | 1358.5255 | 1790.2452 | 2202.5879 | 3183.8394 | 5928.9656 | 9839.5603
9.7 | 66.808 | 69.9049 | 71.0626 | 76.6272 | 96.0281 | 127.1889 | 192.2598 | 382.7281 | 9.7 | 89.725 | 91.5831 | 93.9393 | 100.7405 | 123.5229 | 162.9321 | 241.7504 | 482.1618 | 493.0374 | 9.7 | 126.8876 | 129.9845 | 135.9831 | 145.2574 | 174.8464 | 225.2535 | 326.0676 | 635.1964 | 9.7 | 32.9564 |  | 9.7 | 76.0986 |  | 9.7 | 2414.9599 | 2971.4675 | 3572.1546 | 4709.1973 | 7997.7144 | 11560.3756 | 9.7 | 1358.5255 | 1790.2452 | 2202.5879 | 3183.8394 | 5928.9656 | 9839.5603
9.8 | 64.9499 | 69.9049 | 71.0626 | 76.6272 | 96.0281 | 127.1889 | 192.2598 | 382.7281 | 9.8 | 87.8668 | 91.5831 | 93.9393 | 100.7405 | 123.5229 | 159.2661 | 241.7504 | 482.1618 | 493.0374 | 9.8 | 126.8876 | 129.9845 | 135.9831 | 145.2574 | 174.8464 | 225.2535 | 326.0676 | 635.1964 | 9.8 | 32.9564 |  | 9.8 | 76.0986 |  | 9.8 | 2414.9599 | 2971.4675 | 3572.1546 | 4709.1973 | 7997.7144 | 11560.3756 | 9.8 | 1358.5255 | 1790.2452 | 2202.5879 | 3183.8394 | 5928.9656 | 9615.1354
9.9 | 64.9499 | 69.9049 | 71.0626 | 76.6272 | 96.0281 | 127.1889 | 192.2598 | 382.7281 | 9.9 | 87.8668 | 89.725 | 93.9393 | 100.7405 | 123.5229 | 159.2661 | 241.7504 | 482.1618 | 493.0374 | 9.9 | 126.8876 | 129.9845 | 135.9831 | 142.166 | 171.1805 | 225.2535 | 326.0676 | 635.1964 | 9.9 | 32.9564 |  | 9.9 | 76.0986 |  | 9.9 | 2359.9292 | 2971.4675 | 3572.1546 | 4709.1973 | 7997.7144 | 11560.3756 | 9.9 | 1327.5223 | 1790.2452 | 2202.5879 | 3183.8394 | 5928.9656 | 9615.1354
10 | 64.9499 | 69.9049 | 71.0626 | 76.6272 | 96.0281 | 127.1889 | 192.2598 | 382.7281 | 10 | 87.8668 | 89.725 | 93.9393 | 100.7405 | 123.5229 | 159.2661 | 241.7504 | 482.1618 | 493.0374 | 10 | 123.7907 | 129.9845 | 135.9831 | 142.166 | 171.1805 | 220.671 | 326.0676 | 635.1964 | 10 | 32.9564 |  | 10 | 74.8599 |  | 10 | 2359.9292 | 2904.0355 | 3490.7712 | 4709.1973 | 7997.7144 | 11296.9787 | 10 | 1327.5223 | 1790.2452 | 2202.5879 | 3111.757 | 5928.9656 | 9615.1354

## Earth Grid Calcs (hidden)
Soil resistivity |  | ρ1 | 0
|  | ρ2 | 0
|  | Depth | 0
HV
Earth rod details:
Apparent Soil Res (Ohm.m) (Eqn 7-7 EG-1) |  |  | 0
Radius "r" of rod/s (m) |  |  | 0
Length "L" of rod/s (m) |  |  | 0
Insulated to depth "h" (m) |  |  | 0
Number of rods |  |  | 0
Single rod resistance |  |  | #DIV/0!
Multiplying factor for N rods |  |  | 1
Combined resistance |  |  | #DIV/0!
LV |  |  | TRUE
Earth rod details:
Apparent Soil Res (Ohm.m) (Eqn 7-7 EG-1) |  |  | #DIV/0!
Radius "r" of rod/s (m) |  |  | 0.0075
Length "L" of rod/s (m) |  |  | 2.4
Number of rods |  |  | 2
Single rod resistance |  |  | #DIV/0!
Multiplying factor for N rods |  |  | 0.58529
Combined LV resistance |  |  | #DIV/0!
MEN
Number of Customers |  |  | 0
Applicable soil resistivity |  |  | 0
Parallel Electrodes |  |  | #DIV/0!
2067 Figures Scaled |  |  | #DIV/0!
EE's MEN Model |  |  | #DIV/0!
Total MEN resistance (Ohms) |  |  | #DIV/0!
MEN input numbers (n)
F Factor
10 | 1.006
20 | 1.012
40 | 1.024
60 | 1.036
80 | 1.048
100 | 1.06
150 | 1.09
200 | 1.12
250 | 1.15
300 | 1.18
350 | 1.21
400 | 1.24
500 | 1.3
600 | 1.36
700 | 1.42
800 | 1.48
900 | 1.54
1000 | 1.6
1250 | 1.75
1500 | 1.899
1750 | 2.024
2000 | 2.149
2500 | 2.399
3000 | 2.399
3500 | 2.399
4000 | 2.399
5000 | 2.399
Input No. | 1
Note on I31: Terry Niemeier: if depth is <2m then the maximum of the two layers is taken, else the surface layer is used

## Fault current calcs (hidden)
Feeder nominal voltage kV |  |  |  | 0
System parameters |  |  | config | 0
|  |  | metallic return | 0
Fault Level (kA) |  |  |  | 0
Asssumed percentage of fault current in metallic return (CMEN) |  |  |  | 57.5%
Source Impedance (Ohms) |  |  |  | #DIV/0!
Metallic return impedance |  |  |  | #DIV/0! |  |  |  | #DIV/0!
MEN Impedance |  |  |  | #DIV/0!
HV Earth grid resistance (Ohms) |  |  |  | #DIV/0!
Effective Local Resistance (Ohms) |  |  |  | #DIV/0!
LV Earth grid resistance (Ohms) |  |  |  | #DIV/0!
LV ¦¦ MEN combined earthing (Ohms) |  |  |  | #DIV/0!
Applicable Impedance to ground (Ohms) |  |  |  | #DIV/0!
Min Loop impedance total (hazards) |  |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0!
Max total fault current |  |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0!
Max fault current into earth |  |  |  | #DIV/0! |  |  | #DIV/0! | #DIV/0!
Max EPR (V) |  |  |  | #DIV/0! |  |  | #DIV/0! | Uses voltage factor c = 1.1 as per AS3851
Max Loop impedance (protection) (Ohms) |  |  |  | #DIV/0! |  |  | #DIV/0!
Min fault current seen by protection (Amps) |  |  |  | #DIV/0! | Used to calculate protection clearance time |  |  | Uses voltage factor c = 0.9
Clearance time |  |  |  | 0
HV - LV Fault current |  |  |  | #DIV/0!
Maximum fault current through HV earth grid (A) |  |  |  | #DIV/0! | #DIV/0!
Maximum fault current through effective local earth (A) |  |  |  | #DIV/0! | #DIV/0!
Maximum fault current through MEN (A) |  |  |  | 0 |  |  | 0
Maximum fault current in metallic return |  |  |  | 0 |  |  | 0
Voltage Profile | [5 empty] | Step and Touch
31
0 | #VALUE!
0.5 | #VALUE!
1 | #VALUE! | #VALUE!
1.5 | #VALUE! | #VALUE!
2 | #VALUE! | #VALUE!
2.5 | #VALUE! | #VALUE!
3 | #VALUE! | #VALUE!
3.5 | #VALUE! | #VALUE!
4 | #VALUE! | #VALUE!
4.5 | #VALUE! | #VALUE!
5 | #VALUE! | #VALUE!
5.5 | #VALUE! | #VALUE!
6 | #VALUE! | #VALUE!
6.5 | #VALUE! | #VALUE!
7 | #VALUE! | #VALUE!
7.5 | #VALUE! | #VALUE!
8 | #VALUE! | #VALUE!
8.5 | #VALUE! | #VALUE!
9 | #VALUE! | #VALUE!
9.5 | #VALUE! | #VALUE!
10 | #VALUE! | #VALUE!
10.5 | #VALUE! | #VALUE!
11 | #VALUE! | #VALUE!
11.5 | #VALUE! | #VALUE!
12 | #VALUE! | #VALUE!
12.5 | #VALUE! | #VALUE!
13 | #VALUE! | #VALUE!
13.5 | #VALUE! | #VALUE!
14 | #VALUE! | #VALUE!
14.5 | #VALUE! | #VALUE!
15 | #VALUE! | #VALUE!
15.5 | #VALUE! | #VALUE!
16 | #VALUE! | #VALUE!
16.5 | #VALUE! | #VALUE!
17 | #VALUE! | #VALUE!
17.5 | #VALUE! | #VALUE!
18 | #VALUE! | #VALUE!
18.5 | #VALUE! | #VALUE!
19 | #VALUE! | #VALUE!
19.5 | #VALUE! | #VALUE!
20 | #VALUE! | #VALUE!
20.5 | #VALUE!
21 | #VALUE!
21.5 | #VALUE!
22 | #VALUE!
22.5 | #VALUE!
23 | #VALUE!
23.5 | #VALUE!
24 | #VALUE!
24.5 | #VALUE!
25 | #VALUE!
25.5 | #VALUE!
26 | #VALUE!
26.5 | #VALUE!
27 | #VALUE!
27.5 | #VALUE!
28 | #VALUE!
28.5 | #VALUE!
29 | #VALUE!
29.5 | #VALUE!
30 | #VALUE!
30.5 | #VALUE!
31 | #VALUE!
31.5 | #VALUE!
32 | #VALUE!
32.5 | #VALUE!
33 | #VALUE!
33.5 | #VALUE!
34 | #VALUE!
34.5 | #VALUE!
35 | #VALUE!
35.5 | #VALUE!
36 | #VALUE!
36.5 | #VALUE!
37 | #VALUE!
37.5 | #VALUE!
38 | #VALUE!
38.5 | #VALUE!
39 | #VALUE!
39.5 | #VALUE!
40 | #VALUE!
40.5 | #VALUE!
41 | #VALUE!
41.5 | #VALUE!
42 | #VALUE!
42.5 | #VALUE!
43 | #VALUE!
43.5 | #VALUE!
44 | #VALUE!
44.5 | #VALUE!
45 | #VALUE!
45.5 | #VALUE!
46 | #VALUE!
46.5 | #VALUE!
47 | #VALUE!
47.5 | #VALUE!
48 | #VALUE!
48.5 | #VALUE!
49 | #VALUE!
49.5 | #VALUE!
50 | #VALUE!
50.5 | #VALUE!
51 | #VALUE!
51.5 | #VALUE!
52 | #VALUE!
52.5 | #VALUE!
53 | #VALUE!
53.5 | #VALUE!
54 | #VALUE!
54.5 | #VALUE!
55 | #VALUE!
55.5 | #VALUE!
56 | #VALUE!
56.5 | #VALUE!
57 | #VALUE!
57.5 | #VALUE!
58 | #VALUE!
58.5 | #VALUE!
59 | #VALUE!
59.5 | #VALUE!
60 | #VALUE!
60.5 | #VALUE!
61 | #VALUE!
61.5 | #VALUE!
62 | #VALUE!
62.5 | #VALUE!
63 | #VALUE!
63.5 | #VALUE!
64 | #VALUE!
64.5 | #VALUE!
65 | #VALUE!
65.5 | #VALUE!
66 | #VALUE!
66.5 | #VALUE!
67 | #VALUE!
67.5 | #VALUE!
68 | #VALUE!
68.5 | #VALUE!
69 | #VALUE!
69.5 | #VALUE!
70 | #VALUE!
70.5 | #VALUE!
71 | #VALUE!
71.5 | #VALUE!
72 | #VALUE!
72.5 | #VALUE!
73 | #VALUE!
73.5 | #VALUE!
74 | #VALUE!
74.5 | #VALUE!
75 | #VALUE!
75.5 | #VALUE!
76 | #VALUE!
76.5 | #VALUE!
77 | #VALUE!
77.5 | #VALUE!
78 | #VALUE!
78.5 | #VALUE!
79 | #VALUE!
79.5 | #VALUE!
80 | #VALUE!
80.5 | #VALUE!
81 | #VALUE!
81.5 | #VALUE!
82 | #VALUE!
82.5 | #VALUE!
83 | #VALUE!
83.5 | #VALUE!
84 | #VALUE!
84.5 | #VALUE!
85 | #VALUE!
85.5 | #VALUE!
86 | #VALUE!
86.5 | #VALUE!
87 | #VALUE!
87.5 | #VALUE!
88 | #VALUE!
88.5 | #VALUE!
89 | #VALUE!
89.5 | #VALUE!
90 | #VALUE!
90.5 | #VALUE!
91 | #VALUE!
91.5 | #VALUE!
92 | #VALUE!
92.5 | #VALUE!
93 | #VALUE!
93.5 | #VALUE!
94 | #VALUE!
94.5 | #VALUE!
95 | #VALUE!
95.5 | #VALUE!
96 | #VALUE!
96.5 | #VALUE!
97 | #VALUE!
97.5 | #VALUE!
98 | #VALUE!
98.5 | #VALUE!
99 | #VALUE!
99.5 | #VALUE!
100 | #VALUE!
101 | #VALUE!
102 | #VALUE!
103 | #VALUE!
104 | #VALUE!
105 | #VALUE!
106 | #VALUE!
107 | #VALUE!
108 | #VALUE!
109 | #VALUE!
110 | #VALUE!
111 | #VALUE!
112 | #VALUE!
113 | #VALUE!
114 | #VALUE!
115 | #VALUE!
116 | #VALUE!
117 | #VALUE!
118 | #VALUE!
119 | #VALUE!
120 | #VALUE!
121 | #VALUE!
122 | #VALUE!
123 | #VALUE!
124 | #VALUE!
125 | #VALUE!
126 | #VALUE!
127 | #VALUE!
128 | #VALUE!
129 | #VALUE!
130 | #VALUE!
131 | #VALUE!
132 | #VALUE!
133 | #VALUE!
134 | #VALUE!
135 | #VALUE!
136 | #VALUE!
137 | #VALUE!
138 | #VALUE!
139 | #VALUE!
140 | #VALUE!
141 | #VALUE!
142 | #VALUE!
143 | #VALUE!
144 | #VALUE!
145 | #VALUE!
146 | #VALUE!
147 | #VALUE!
148 | #VALUE!
149 | #VALUE!
150 | #VALUE!
151 | #VALUE!
152 | #VALUE!
153 | #VALUE!
154 | #VALUE!
155 | #VALUE!
156 | #VALUE!
157 | #VALUE!
158 | #VALUE!
159 | #VALUE!
160 | #VALUE!
161 | #VALUE!
162 | #VALUE!
163 | #VALUE!
164 | #VALUE!
165 | #VALUE!
166 | #VALUE!
167 | #VALUE!
168 | #VALUE!
169 | #VALUE!
170 | #VALUE!
171 | #VALUE!
172 | #VALUE!
173 | #VALUE!
174 | #VALUE!
175 | #VALUE!
176 | #VALUE!
177 | #VALUE!
178 | #VALUE!
179 | #VALUE!
180 | #VALUE!
181 | #VALUE!
182 | #VALUE!
183 | #VALUE!
184 | #VALUE!
185 | #VALUE!
186 | #VALUE!
187 | #VALUE!
188 | #VALUE!
189 | #VALUE!
190 | #VALUE!
191 | #VALUE!
192 | #VALUE!
193 | #VALUE!
194 | #VALUE!
195 | #VALUE!
196 | #VALUE!
197 | #VALUE!
198 | #VALUE!
199 | #VALUE!
200 | #VALUE!
201 | #VALUE!
202 | #VALUE!
203 | #VALUE!
204 | #VALUE!
205 | #VALUE!
206 | #VALUE!
207 | #VALUE!
208 | #VALUE!
209 | #VALUE!
210 | #VALUE!
211 | #VALUE!
212 | #VALUE!
213 | #VALUE!
214 | #VALUE!
215 | #VALUE!
216 | #VALUE!
217 | #VALUE!
218 | #VALUE!
219 | #VALUE!
220 | #VALUE!
221 | #VALUE!
222 | #VALUE!
223 | #VALUE!
224 | #VALUE!
225 | #VALUE!
226 | #VALUE!
227 | #VALUE!
228 | #VALUE!
229 | #VALUE!
230 | #VALUE!
231 | #VALUE!
232 | #VALUE!
233 | #VALUE!
234 | #VALUE!
235 | #VALUE!
236 | #VALUE!
237 | #VALUE!
238 | #VALUE!
239 | #VALUE!
240 | #VALUE!
241 | #VALUE!
242 | #VALUE!
243 | #VALUE!
244 | #VALUE!
245 | #VALUE!
246 | #VALUE!
247 | #VALUE!
248 | #VALUE!
249 | #VALUE!
250 | #VALUE!
251 | #VALUE!
252 | #VALUE!
253 | #VALUE!
254 | #VALUE!
255 | #VALUE!
256 | #VALUE!
257 | #VALUE!
258 | #VALUE!
259 | #VALUE!
260 | #VALUE!
261 | #VALUE!
262 | #VALUE!
263 | #VALUE!
264 | #VALUE!
265 | #VALUE!
266 | #VALUE!
267 | #VALUE!
268 | #VALUE!
269 | #VALUE!
270 | #VALUE!
271 | #VALUE!
272 | #VALUE!
273 | #VALUE!
274 | #VALUE!
275 | #VALUE!
276 | #VALUE!
277 | #VALUE!
278 | #VALUE!
279 | #VALUE!
280 | #VALUE!
281 | #VALUE!
282 | #VALUE!
283 | #VALUE!
284 | #VALUE!
285 | #VALUE!
286 | #VALUE!
287 | #VALUE!
288 | #VALUE!
289 | #VALUE!
290 | #VALUE!
291 | #VALUE!
292 | #VALUE!
293 | #VALUE!
294 | #VALUE!
295 | #VALUE!
296 | #VALUE!
297 | #VALUE!
298 | #VALUE!
299 | #VALUE!
300 | #VALUE!
301 | #VALUE!
302 | #VALUE!
303 | #VALUE!
304 | #VALUE!
305 | #VALUE!
306 | #VALUE!
307 | #VALUE!
308 | #VALUE!
309 | #VALUE!
310 | #VALUE!
311 | #VALUE!
312 | #VALUE!
313 | #VALUE!
314 | #VALUE!
315 | #VALUE!
316 | #VALUE!
317 | #VALUE!
318 | #VALUE!
319 | #VALUE!
320 | #VALUE!
321 | #VALUE!
322 | #VALUE!
323 | #VALUE!
324 | #VALUE!
325 | #VALUE!
326 | #VALUE!
327 | #VALUE!
328 | #VALUE!
329 | #VALUE!
330 | #VALUE!
331 | #VALUE!
332 | #VALUE!
333 | #VALUE!
334 | #VALUE!
335 | #VALUE!
336 | #VALUE!
337 | #VALUE!
338 | #VALUE!
339 | #VALUE!
340 | #VALUE!
341 | #VALUE!
342 | #VALUE!
343 | #VALUE!
344 | #VALUE!
345 | #VALUE!
346 | #VALUE!
347 | #VALUE!
348 | #VALUE!
349 | #VALUE!
350 | #VALUE!
351 | #VALUE!
352 | #VALUE!
353 | #VALUE!
354 | #VALUE!
355 | #VALUE!
356 | #VALUE!
357 | #VALUE!
358 | #VALUE!
359 | #VALUE!
360 | #VALUE!
361 | #VALUE!
362 | #VALUE!
363 | #VALUE!
364 | #VALUE!
365 | #VALUE!
366 | #VALUE!
367 | #VALUE!
368 | #VALUE!
369 | #VALUE!
370 | #VALUE!
371 | #VALUE!
372 | #VALUE!
373 | #VALUE!
374 | #VALUE!
375 | #VALUE!
376 | #VALUE!
377 | #VALUE!
378 | #VALUE!
379 | #VALUE!
380 | #VALUE!
381 | #VALUE!
382 | #VALUE!
383 | #VALUE!
384 | #VALUE!
385 | #VALUE!
386 | #VALUE!
387 | #VALUE!
388 | #VALUE!
389 | #VALUE!
390 | #VALUE!
391 | #VALUE!
392 | #VALUE!
393 | #VALUE!
394 | #VALUE!
395 | #VALUE!
396 | #VALUE!
397 | #VALUE!
398 | #VALUE!
399 | #VALUE!
400 | #VALUE!
401 | #VALUE!
402 | #VALUE!
403 | #VALUE!
404 | #VALUE!
405 | #VALUE!
406 | #VALUE!
407 | #VALUE!
408 | #VALUE!
409 | #VALUE!
410 | #VALUE!
411 | #VALUE!
412 | #VALUE!
413 | #VALUE!
414 | #VALUE!
415 | #VALUE!
416 | #VALUE!
417 | #VALUE!
418 | #VALUE!
419 | #VALUE!
420 | #VALUE!
421 | #VALUE!
422 | #VALUE!
423 | #VALUE!
424 | #VALUE!
425 | #VALUE!
426 | #VALUE!
427 | #VALUE!
428 | #VALUE!
429 | #VALUE!
430 | #VALUE!
431 | #VALUE!
432 | #VALUE!
433 | #VALUE!
434 | #VALUE!
435 | #VALUE!
436 | #VALUE!
437 | #VALUE!
438 | #VALUE!
439 | #VALUE!
440 | #VALUE!
441 | #VALUE!
442 | #VALUE!
443 | #VALUE!
444 | #VALUE!
445 | #VALUE!
446 | #VALUE!
447 | #VALUE!
448 | #VALUE!
449 | #VALUE!
450 | #VALUE!
451 | #VALUE!
452 | #VALUE!
453 | #VALUE!
454 | #VALUE!
455 | #VALUE!
456 | #VALUE!
457 | #VALUE!
458 | #VALUE!
459 | #VALUE!
460 | #VALUE!
461 | #VALUE!
462 | #VALUE!
463 | #VALUE!
464 | #VALUE!
465 | #VALUE!
466 | #VALUE!
467 | #VALUE!
468 | #VALUE!
469 | #VALUE!
470 | #VALUE!
471 | #VALUE!
472 | #VALUE!
473 | #VALUE!
474 | #VALUE!
475 | #VALUE!
476 | #VALUE!
477 | #VALUE!
478 | #VALUE!
479 | #VALUE!
480 | #VALUE!
481 | #VALUE!
482 | #VALUE!
483 | #VALUE!
484 | #VALUE!
485 | #VALUE!
486 | #VALUE!
487 | #VALUE!
488 | #VALUE!
489 | #VALUE!
490 | #VALUE!
491 | #VALUE!
492 | #VALUE!
493 | #VALUE!
494 | #VALUE!
495 | #VALUE!
496 | #VALUE!
497 | #VALUE!
498 | #VALUE!
499 | #VALUE!
500 | #VALUE!

## substations (hidden)
substation | sub requirements | Equipment List | Fuses
Abbotsbury |  | Padmount Substation | 3.15
Albion Park |  | Pole Mounted Substation | 8
Ambarvale |  | Auto-Recloser | 16
Anzac Village |  | Load Break Switch | 20
Appin |  | Switching Station | 40
Arndell Park |  | UGOH | 100
Baulkham Hills |  | Regulator
Bella Vista |  | Other
Berrima Junction
Berry
Blackheath
Blackmans Flat
Blaxland
Bolong
Bomaderry
Bonnyrigg
Bossley Park
Bow Bowing
Bowral
Bringelly
Bulli
Bylong
Cabramatta
Cambridge Park
Campbelltown
Canley Vale
Carramar
Castle Hill
Casula
Cattai
Cawdor
Cheriton Avenue
Chipping Norton
Claremont Meadows
Corrimal
Cranebrook
Culburra
Dapto
Darkes Forest
Doonside
Dundas
East Richmond
Eastern Creek
Edmonson Park
Emu Plains
Erskine Park
Fairfield
Figtree
Gerringong
Glenmore Park
Glenorie
Glossodia
Granville
Greystanes
Hartley Vale
Hazelbrook
Helensburgh
Hinchinbrook
Holroyd
Homepride
Horsley Park
Hoxton Park
Huntingwood
Huskisson
Ilford Hall
Inner Harbour
Jamberoo
Jasper Road
Jordan Springs
Kandos
Kangaroo Valley
Katoomba
Kellyville
Kembla Grange
Kemps Creek
Kenny Street
Kenthurst
Kentlyn
Kiama
Kingswood
Kurrajong
Leabons Lane
Lennox
Lithgow
Liverpool
Luddenham
Macquarie Fields
Maldon
Mamre
Marayong
Meadow flat
Minto
Mittagong
Moorebank
Moss Vale
Mount Ousley
Mungerie Park
Narellan
Nepean
Newton
North Eastern Creek
North Parramatta
North Richmond
North Rocks
North Warragamba
North Wollongong
Northmead
Nowra
Oakdale
Oran Park
Parklea
Parramatta
Penrith
Plumpton
Port Central
Port Kembla
Portland
Prestons
Prospect
Quakers Hill
Quarries
Richmond
Ringwood
Riverstone
Robertson
Rooty Hill
Rosehill
Russell Vale
Rydalmere
Schofields
Seven Hills
Shellharbour
Sherwood
Schofields
Smithfield
South Granville
South Leppington
South Nowra
South Windsor
South Wollongong
Springwood
St Marys
Sussex Inlet
Tahmoor
The Oaks
Tomerong
Ulladulla
Unanderra
Warilla
Wentworth Falls
Werrington
West Castle Hill
West Liverpool
West Parramatta
West Pennant Hills
West Wetherill Park
West Wollongong
Westmead
Wetherill Park
Whalan
Wilton
Windsor
Wisemans
Wombarra
Woodpark
Yatte Yattah
Yennora
other

## Field Checksheet (hidden)
Date:
Earthing Design - Field Checksheet
Location:
Designer:
Feeder:
Rate Voltage:
Equipment Type:
Location Type: | Normal / Remote / Special
Fences In Area?
Sketch fence location relative to installation
Communications Assets In Area?
Sketch location of communications assets relative to installation:
Any other special constraints in the area?

## Help
Revision History |  | Rev
2012-02-01 | Added help file and fixed confusing units | 1
2012-02-01 | Fixed calculation method for h<0.5 to a per rod method | 1.1
2012-10-01 | Added metallicreturn calculations to main page | 1.2
2013-12-01 | Overhall of sheet to meet requirements of EDI100 | 2
2014-09-01 | • Added user sef pick up • Clearer indication of pass or fail for common earthed designs • Update terminology • Change soil res to require minimum values • Changed soil res to drop down selections • Fixed LV rod issue • Show required LV/HV electrode separation (requires No. of connected MEN to be entered for Common or Seperately earthed designs) | 2.2a-b
2015-01-01 | • Ticks removed (side bar shows common earth status) • Side bar shows status of design and if the sheet has been filled • Locked soil res calculator to require valid input, otherwise sheet wont work • Update LV/HV separation to give minimum of 4m even if distance to MEN is 0m • Update to formatting so sheet can be printed • Design will show if it is seperately or common earthed • Update to protection to cater for instantaneous protection settings | 2.3
2015-01-01 | • Project field was locked (now unlocked) • Latitude/Longitude field formatting fixed • Issues with "DESIGN INCOMPLETE" rectifed • Isssue with blank protection values fixed • Notes field added | 2.3a
2015-08-01 | • Updated LV/HV to accommodate HV & LV electrode length when customers > 4 • Issue with single rod resistance and insulated layer fixed | 2.3b
2016-03-01 | • Update to protection calculations to allow for IEC 60255 trip time calculations • Enforcement of GPS location for soil resistivity location • Ability to store soil resistivity readings taken by Endeavour Energy Staff (for comparison) • View location of soil test in google maps • Version check on main sheet for Endeavour Energy Staff • Update to protection input to allow for advance input and additional relays • Update Backyard scenario to match EDI0001 and EG(0) • Update calculations using Max and Min fault current • ALARP Design sheet and check added | 2.5 (Version 2.4 was not released)
2017-05-01 | • Enforcement of two soil resistivity test results with at least 20m spacings entered • Updated check CMEN warning • Addition of validating design with actual commissioning test results • Updated GPR to EPR to reflect Australian industry terminology • Removal of School limit as this should be assessed on a case by case scenario by the designer • Fix bug in DOF clearing time for 3A, 20A and 40A | 2.6