## Sheet1
[5 empty] | ROUND DUCT ORDER SHEET | [16 empty] | 5
Straight Duct with Straight Tap (Not for use with 2" (50.4) & 3" (76.2) EZ Taps)
TAP SPECIFICATIONS
[6 empty] | -D1- | -L1- |  | -D1- | -D2- | -D3- |  | -L2- |  | -L3- | -D3- | -A1-
[6 empty] | DUCT | DUCT |  | RING | RING | TAP |  | LOCATE |  | TAP | RING | TAP
FITTING NUMBER |  |  |  | QTY |  | DIA | LENGTH |  | TYPE | TYPE | DIA |  | FROM D1 |  | LENGTH | TYPE | ANGLE |  | REMARKS
"L1" MIN = ( "D3" + 8" (203.2)) • "L1 MAX = 96-1/4" (2444.8) • "D3 MAX = 88" (2235.2)
STRAIGHT TAP GREATER THAN 88" (2235.2) [ "D3" ] REQUIRES 2 PIECE DESIGN AND ENGINEERING REVIEW
STANDARD DUCT LENGTHS ("L1")
RING | DIAMETER |  |  |  | "L1"=4' (1219.2) |  |  | "L1"=8' (2438.4) |  |  |  | RING |  | DIAMETER |  |  |  | "L1"=4' (1219.2) |  |  | "L1"=8' (2438.4)
EZ/SC | 4" (101.6) & 6" (152.4) |  |  |  | 47.25" (1200.5) |  |  | NA |  |  |  | BI/SS |  | 16" (406.4) TO 48" (1219.2) |  |  |  | 47.25" (1200.5) |  |  | 95.25" (2419.35)
EZ/SC | 8" (203.2) TO 14" (355.6) |  |  |  | 47.25" (1200.5) |  |  | 95.25" (2419.35) |  |  |  | BI/SS |  | 50" (1270) TO 120" (3048) |  |  |  | 46.75" (1187.45) |  |  | 94.75" (2406.65)
NOTES: |  | 1 | SEE THE STANDARDS SECTION OF THE PRODUCT CATALOG FOR INFORMATION ABOUT | [14 empty] | DUCT JOINT / RING TYPE
DUCT GAUGE, RING MECHANICAL SPECS, HARDWARE AND GASKETS.
|  | 2 | OPTION: CUSTOM LENGTH | [14 empty] | EZ |  | EZ CLAMP
|  | 3 | OPTION: RAW END | [16 empty] | 4"Ø-14"Ø (101.6-355.6)
|  | 4 | OPTION: MULTIPLE / OFFSET TAPS (SEE MULTIPLE TAP SHEET) | [14 empty] | SC |  | STAINLESS CAST RING
|  | 5 | DUCT GREATER THAN 84" DIA. (2133.6mm) REQUIRES ENGINEERING REVIEW AND | [16 empty] | 4"Ø-14"Ø (101.6-355.6)
|  |  | APPROVAL. | [14 empty] | BI |  | BLACK IRON ANGLE RING
|  | 6 | OUR RECOMMENDATION IS TO ADD TAPS TO STANDARD 4' (1219.2) AND 8' (2438.4) DUCT | [16 empty] | 16"Ø-120"Ø (406.4-3048.0)
|  |  | WHEN POSSIBLE - TAP DIMENSIONS SHOWN ARE MINS. LONGER THAN STANDARD | [14 empty] | SS |  | STAINLESS ANGLE RING
|  |  | LENGTHS AND/OR HIGHER SYSTEM PRESSURE MAY REQUIRE ADDITIONAL STIFFENERS | [16 empty] | 4"Ø-128"Ø (101.6-3251.2)
PER SMACNA, SPECIFIC GUIDELINES AVAILABLE.
|  | 7 | ALL DUCT FITTINGS WITH STANDARD CONNECTIONS INCLUDE GASKETS AND CLAMPS
OR HARDWARE AS REQUIRED FOR INSTALLATION.
METRIC EQUIVALENTS ARE SHOWN IN PARENTHESIS & ITALICS (MILLIMETERS OR AS NOTED)
REMARKS:
COMPANY / JOB REFERENCE:
Exential U.S. Inc. ¦ T 802-655-8800 ¦ F 802-655-8804 ¦ www.exentec.net/products/process-exhaust
© COPYRIGHT 2025 EXENTIAL U.S. INC. REV: 01/01/25 RND005BF | [21 empty] | 5