## Sheet1
[5 empty] | ROUND DUCT ORDER SHEET | [13 empty] | 12
Reducers
[6 empty] | -D1- | -D2- |  | -L1- | -L2- | -L3- |  | -D1- | -D2-
[6 empty] | DUCT | DUCT |  | DUCT | TAPER | CENTER |  | RING | RING
FITTING NUMBER |  |  | QTY |  |  | DIA | DIA |  | LENGTH | LENGTH | OFFSET |  | TYPE | TYPE | REMARKS
ECCENTRIC | [7 empty] | CONCENTRIC | [6 empty] | MIN "L4" / "L5"
AMOUNT OF REDUCTION |  |  |  | MINIMUM |  |  |  | AMOUNT OF REDUCTION |  |  |  | MINIMUM |  |  | DUCT DIAMETER |  |  | MINIMUM
"D1" minus "D2" |  |  |  | "L2" |  |  |  | "D1" minus "D2" |  |  |  | "L2" |  |  | "D1" or "D2" |  |  | "L4 or "L5"
6" (152.4) AND LESS |  |  |  | 12" (304.8) |  |  |  | 9" (228.6) AND LESS |  |  |  | 12" (304.8) |  |  | 4" (101.6) TO 58" (1473.2) |  |  | 3" (76.2)
7" (177.8) TO 9" (288.6) |  |  |  | 18" (457.2) |  |  |  | 10" (254.0) TO 14" (355.6) |  |  |  | 18" (457.2) |  |  | 60" (1524.0) TO 94" (2387.6) |  |  | 4" (101.6)
10" (254.0) TO 13" (330.2) |  |  |  | 24" (609.6) |  |  |  | 15" (381.0) TO 19" (482.6) |  |  |  | 24" (609.6) |  |  | 96" (2438.4) TO 120" (3048.0) |  |  | 5" (127.0)
14" (355.6) TO 17" (431.8) |  |  |  | 30" (762.0) |  |  |  | 20" (508.0) TO 24" (609.6) |  |  |  | 30" (762.0)
DUCT JOINT / RING TYPE
[16 empty] | EZ | EZ CLAMP
NOTES: | 1 | SEE THE STANDARDS SECTION OF THE PRODUCT CATALOG FOR INFORMATION ABOUT | [14 empty] | 4"Ø-14"Ø (101.6-355.6)
|  | DUCT GAUGE, RING MECHANICAL SPECS, HARDWARE AND GASKETS. | [13 empty] | SC | STAINLESS CAST RING
| 2 | OPTION: CUSTOM LENGTHS AVAILABLE | [14 empty] | 4"Ø-14"Ø (101.6-355.6)
| 3 | DUCT GREATER THAN 84" (2133.6mm) REQUIRES ENGINEERING REVIEW AND | [13 empty] | BI | BLACK IRON ANGLE RING
|  | APPROVAL. | [14 empty] | 16"Ø-120"Ø (406.4-3048.0)
| 4 | ALL DUCT FITTINGS WITH STANDARD CONNECTIONS INCLUDE GASKETS AND CLAMPS | [13 empty] | SS | STAINLESS ANGLE RING
|  | OR HARDWARE AS REQUIRED FOR INSTALLATION. | [14 empty] | 4"Ø-128"Ø (101.6-3251.2)
METRIC EQUIVALENTS ARE SHOWN IN PARENTHESIS & ITALICS (MILLIMETERS OR AS NOTED)
REMARKS:
COMPANY / JOB REFERENCE:
Exential U.S. Inc. ¦ T 802-655-8800 ¦ F 802-655-8804 ¦ www.exentec.net/products/process-exhaust
© COPYRIGHT 2025 EXENTAL U.S. INC. REV: 01/01/25 RND012BF | [18 empty] | 12