## HVAC Selection Matrix
CIP BUILDING ELECTRIFICATION EQUIPMENT SELECTION MATRIX
Legend
BUILDING ID: | [6 empty] | Drop-down menu
PROJECT SCOPE: | [6 empty] | Automated field
Answer all questions in sequence using the BCAS report as an initial reference. Conditions observed in the field will supersede the BCAS report. | [6 empty] | Manual Input
Heating Plant Decision Matrix (when HEATING PLANT replacement is the original CIP project)
1) | Do boilers have more than 15 year life?
1a) | Do boilers run on oil or gas or dual fuel?
Cooling Plant Decision Matrix (when COOLING PLANT replacement is the original CIP project)
1) | Do the PA spaces have central AC?
*-Window Units and AC Split Units are not considered for equipment selection matrix.
2) | Do the Cooling plant/boilers have more than 15 year life?
3) | What is the existing cooling equipment type for all spaces?
| Classroom/Offices Equipment | PA Spaces Equipment | Other Equipment
HEAT PUMP SELECTION TABLE |  | Grading System: 1- Optimal Option, 0- Possible Option, T-Terminal (Not Feasible)
| CLASSROOMS & OFFICES |  |  | Options
| Existing Conditions |  | Yes/No | Central RTU/Heat Pumps (includes electric baseboard in spaces) | Central Split/DX Heat Pumps in interior MER (includes electric baseboard in spaces) | DX VUV-Packaged Heat Pumps w/ERV | Chiller Heater/Dual Temp Rooftop DOAS with Fan Coil Units in the Spaces | Chiller Heater/Dual Temp MER DOAS with Fan Coil Units in the Spaces | Chiller/Heater/ Dual Temp VUVs w/ERV | DX VUV-Split Heat Pumps w/ERV w/Rooftop Outdoor Units | VRF w/DOAS | Logic
| Roof more than 15 years old and existing equipment is on dunnage? | [10 empty] | Roofs older than 15 years old should have systems installed that require less rooftop equipment. However, roofs that are older than 15 years old should be strongly considered for replacement as an added scope. Ceiling VRF option is limited to buildings 20,000 SF or less due to operational maintenance requirements. Additionally, split DX systems are not preferred due to the number of mechanical piping connections constructed in the field.
| Utilization rate less than 80%? | [10 empty] | Schools with low utilization rates allow for more swing space and create potential for renovating larger areas at a time which favors central systems.
| MER in future floodplain for year 2100 (NYC Flood Hazard Mapper)? | [10 empty] | The Interior MER is assumed to be sufficiently large to accommodate any of the proposed systems. If the existing boiler rooms that are no longer being used are below the floodplain, then that vacant sq/ft is not available to put new mechanical equipment. (T for Interior fan rooms below floodplain.)
| Structural floor to ceiling/beams below 9'? | [10 empty] | Ducting for central systems or above unit ventilators is not feasible at these low floor to ceiling/beam heights.
| Cinder concrete slabs/clay tile arch? (duct anchorage to be discussed with CM) | [10 empty] | Cinder Concrete slabs cannot take large point loads at the roof or individual floors, which makes VUV and roof mounted equipment installation more difficult. When cinder concrete is present, VUVs shall utilize ductless free delivery supply to avoid the need for supplementary steel to support supply ductwork. Other HVAC systems supply ductwork may require supplementary steel. Design of VUV with free delivery should consider the need for perimeter heating to avoid temperature gradient.
| SHPO eligible or historically significant? | [10 empty] | SHPO buildings have less ability to make aesthetic changes; however these are not insurmountable.
| Is there existing chilled water distribution system? | [10 empty] | With existing chilled water pipes available, they might (as some systems may not be building wide) be used for both new chilled and heated water.
| Existing chilled water distribution in good condition? | [10 empty] | With existing chilled water pipes available, they might (as some systems may not be building wide) be used for both new chilled and heated water.
| Windows BCAS rating of 4-5, single pane, or more than 30 year old? | [10 empty] | VUV might require window replacement. If need to maintain existing louver dimensions, dual temp VUV vent are preferable to DX VUV. 30 years is the assumed life of the window.
| Windows have narrow widths or most classrooms have only a few windows? | [10 empty] | If windows are too narrow, then unit ventilators don't fit within one window bay and should be avoided. If there are only a few windows in each classroom, avoid unit ventilators to take up prime window space.
| Is there sufficient flat roof area for roof-mounted equipment? | [10 empty] | Systems should not be installed on the pitched roof. Pitched roof favors DOAS located in MER. Flat roof allows roof-mounted DOAS.
|  |  | Classroom and Office System Rating: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Design team to provide cost of the 2 highest rated options as part of draft scope
PUBLIC ASSEMBLY SPACES - AUDITORIUM (options noted below)
| Existing Conditions |  | Yes/No | Central RTU/DX Heat Pumps SZVAV (includes recessed electric convectors in spaces) | Central Split/DX Heat Pumps SZVAV in interior MER (includes recessed electric convectors in spaces) | Chiller Heater Central RTU Dual Temp SZVAV (includes recessed hot water convectors in spaces) | VRF w/DOAS | Chiller Heater/Central AHU Dual Temp SZVAV in interior MER (includes recessed hot water convectors in spaces) | Logic
| Roof more than 15 years old and existing equipment is on dunnage |  | 0 | [5 empty] | Roofs older than 15 years old should have systems installed that require less rooftop equipment. However, roofs that are older than 15 years old should be strongly considered for replacement as an added scope. Ceiling VRF option is limited to buildings 20,000 SF or less due to operational maintenance requirements. Additionally, split DX systems are not preferred due to the number of mechanical piping connections constructed in the field.
| Linear footage > 200 ft between roof and mechanical room serving PA space | [7 empty] | Long refrigerant piping should be avoided since braised piping/fitting may leak.
| MER in future flood plain for year 2100 (NYC Flood Hazard Mapper) |  | 0 | [5 empty] | If the existing boiler rooms that are no longer being used are below the floodplain, then that vacant sq/ft is not available to put new mechanical equipment. (T for Interior fan rooms below floodplain.)
| Ornate and/or historic ceilings in Auditorium | [7 empty] | Limiting ductwork that would not cause the ceilings in these spaces to be rebuilt/modified is preferred.
| PA spaces on lower floors w/classrooms above? | [7 empty] | Limiting ductwork from the roof to the lower PA spaces is preferred in this condition.
| Cinder concrete slabs/clay tile arch? |  | 0 | [5 empty] | Cinder Concrete slabs cannot take large point loads at the roof or individual floors, which makes VUV and roof mounted equipment installation more difficult. When cinder concrete is present, VUVs shall utilize ductless free delivery supply to avoid the need for supplementary steel to support supply ductwork. Other HVAC systems supply ductwork may require supplementary steel. Design of VUV with free delivery should consider the need for perimeter heating to avoid temperature gradient.
| Is there existing chilled water distribution system? |  | 0 | [5 empty] | With existing chilled water pipes available, they can be used for both new chilled and heated water.
| Chilled water distribution in good condition? |  | 0 | [5 empty] | With existing chilled water pipes available, they can be used for both new chilled and heated water.
| Is there sufficient flat roof area above this space for roof-mounted equipment | [7 empty] | Systems should not be installed on the pitched roof. If no flat roof area at all, consider placing condensing units and chiller/heater on grade.
Structural floor to ceiling/beams below 12'?
|  |  | Large Public Assembly System Rating: | 0 | 0 | 0 | 0 | 0
Design team to provide cost of the 2 highest rated options as part of draft scope
PUBLIC ASSEMBLY SPACES - GYM/CAFETERIA (options noted below)
| Existing Conditions |  | Yes/No | Central RTU/DX Heat Pumps SZVAV (includes recessed electric convectors in spaces) | Central Split/DX Heat Pumps SZVAV in interior MER (includes recessed electric convectors in spaces) | Chiller Heater Central RTU Dual Temp SZVAV (includes recessed hot water convectors in spaces) | VRF w/DOAS | Chiller Heater/Central AHU Dual Temp SZVAV in interior MER (includes recessed hot water convectors in spaces) | Logic
| Roof more than 15 years old and existing equipment is on dunnage |  | 0 | [5 empty] | Roofs older than 15 years old should have systems installed that require less rooftop equipment. However, roof that are older than 15 years old should be strongly considered for replacement as an added scope. Ceiling VRF option is limited to buildings 20,000 SF or less due to operational maintenance requirements. Additionally, split DX systems are not preferred due to the number of mechanical piping connections constructed in the field.
| Linear footage > 200 ft between roof and mechanical room serving PA space | [7 empty] | Long refrigerant piping should be avoided since braised piping/fitting may leak. |  |  |  | (1 if Yes) (0 if No) | (T if Yes) (1 if No) | (1 if Yes) (0 if No) | (1 if Yes) (0 if No) | (0 if Yes) (1 if No)
| MER in future flood plain for year 2100 (NYC Flood Hazard Mapper) |  | 0 | [5 empty] | If the existing boiler rooms that are no longer being used are below the floodplain, then that vacant sq/ft is not available to put new mechanical equipment. (T for Interior fan rooms below floodplain.)
| Gym on the top floor? | [7 empty] | Limiting ductwork that would not cause the ceilings in these spaces to be rebuilt/modified is preferred.
| PA spaces on lower floors w/classrooms above? | [7 empty] | Limiting ductwork from the roof to the lower PA spaces is preferred in this condition.
| Cinder concrete slabs/clay tile arch? |  | 0 | [5 empty] | Cinder Concrete slabs cannot take large point loads at the roof or individual floors which makes VUV and roof-mounted equipment installation more difficult. When cinder concrete is present, VUVs shall utilize ductless free delivery supply to avoid the need for supplementary steel to support supply ductwork. Other HVAC systems supply ductwork may require supplementary steel. Design of VUV with free delivery should consider the need for perimeter heating to avoid temperature gradient.
| Is there existing chilled water distribution system? |  | 0 | [5 empty] | With existing chilled water pipes available, they can be used for both new chilled and heated water.
| Chilled water distribution in good condition? |  | 0 | [5 empty] | With existing chilled water pipes available, they can be used for both new chilled and heated water.
| Is there sufficient flat roof area above this space for roof-mounted equipment? | [7 empty] | Systems should not be installed on the pitched roof. If no flat roof area at all, consider placing condensing units and chiller/heater on grade.
| Structural floor to ceiling/beams below 12'? |  | 0
|  |  | Gym/Cafeteria System Rating: | 0 | 0 | 0 | 0 | 0
Design team to provide cost of the 2 highest rated options as part of draft scope
Central Chilled Water Serving fan coil units, units ventilators
Central chilled water serving AHUs/VAV boxes
Central DX serving AHUs/VAV boxes
DX Unit Ventilators
None of the above systems exist
Central chilled water serving AHUs
Central DX AHUs
Central Split DX
Central Chilled Water
None of the above systems exist
Central Chilled Water Air-Cooled
Central Chilled Water Cooled with Cooling Tower

## Reference Tables (hidden)
General
Yes | No
General-2
Yes | No
N/A | Yes
No
Do boilers run on oil or gas?-Part I
Yes | No
N/A | 1. Gas | 3. Oil, burner is not functioning or easily repairable. | 4. Oil, burner is functioning
| 2. Dual Fuel | Replace existing burner with new B100 burner. | Recommend to DSF to revise fuel and change seals if needed
3. Oil, burner is not functioning or easily repairable.
4. Oil, burner is functioning
What is the existing cooling equipment type for all spaces?-Part I
No | Yes
Classrm/office: Central Chilled Water serving fan coil units, unit ventilators | N/A
Classrm/office: Central Chilled water serving AHUs/VAV boxes
Classroom/office: Central DX serving AHUs/VAV boxes
Classroom/office: DX unit ventilators
Classroom/office: Does not exist
PA Space: Central Chilled Water serving AHUs.
PA Space: Central DX AHUs
PA Space: Central Split DX
PA Space: Central Chilled water
PA Space: Does not exist
Central Chilled Water Air-Cooled
Central Chilled Water Cooled with Cooling Tower
General-3
Yes | No
Yes | N/A
No