Existing Building Electrification – PS XXXX

For

NYC School Construction Authority

PS XXXX

D xxxxxxx

X/XX/2024

IMPORTANT NOTE: This document is an example of an Existing Building Report and is intended only as a reference to be used when creating new reports. Certain sections may have been edited or removed to fit this particular school. Data in this report may not pertain to the actual school in question. For modelers, use the Existing Building Report Template, which is a blank version of this report more appropriate for all cases.

Report template version 2.3

April 2024

Table of Contents

1.	Executive Summary	3

2.	Existing Building Model	4

3.	Energy Model Calibration Results	6

4.	Proposed Design Modeling Approach.	8

5.	Estimating Savings from EEMs	9

6.	Comparison of Existing and Proposed Building	10

Appendix A: Side-by-side comparison	12

Appendix B: Energy Model Outputs  - Existing Building TMY3 with Current Utility Rates	23

# Executive Summary

1.1 Existing Building Conditions and Scope of Work:

The existing building is a five-story school building initially constructed in 1993. The fourth and fifth floors were renovated around 1995 and the roofs were replaced in 2015. The envelope is in satisfactory condition. The building was initially served by dual-fuel boilers and primarily using natural gas as fuel. Cooling is provided by an electric chiller. Classrooms were served by unit ventilators and all other spaces were served by air handling units. The scope of modeling is to compare the existing building to the proposed design. Utility bills were provided and the existing building baseline was matched to the bills before EEMs were modeled. The design will also be compared to the LL51/2023 baseline which will follow the 2020 NYCECC using the ASHRAE 90.1-2016 ECB path.

1.2 Proposed Building Upgrades:

The proposed energy efficiency measures (EEMs) that were analyzed were limited to windows, lighting, kitchen equipment, and HVAC upgrades only. They are as follows:

- Window Components

  - U-0.45 fenestration replacement (17% WWR retained)

- Lighting

  - Fluorescent lighting replaced with LEDs in the corridors, mechanical spaces, kitchen, cafeteria, and two classrooms.

- HVAC Equipment

  - Gas boilers are replaced by new heat-pump chillers and supplemental electric boilers

  - AHUs with heat pumps for heating and cooling

  - Energy recovery ventilation

  - Heat pump service water heaters.

- Kitchen equipment

  - Replacement of gas-fired range/ovens with electric range/oven.

1.3 Savings vs. Existing Building Baseline:

- Projected cost savings: $37,325/year

- Projected energy savings

- Electricity savings: 330,131 kWh/year

- Natural gas savings: 42,840 Therms/year

- Building energy use intensity savings (site): 47.1 kBtu/sf.yr

- Building energy use intensity savings (source): 64.2 kBtu/sf.yr

- Building CO2 emissions savings: 300.1 Tons CO2e/year

1.4 Savings vs. Local Law 51 Baseline:

Construction costs for electrifying the HVAC system exceeds $2 million, per the Final Scope Report prepared by Shenoy Engineering for this project. To demonstrate compliance with the NYC LL51/2023 the project must achieve energy use reductions of at least 10% for the renovated HVAC system versus the LL51 baseline. The LL51 baseline is ASHRAE 90.1-2016 ECB as amended in the 2020 NYC ECC.

The energy model results show that the design achieves 11.7% energy use savings for the renovated HVAC system.

| Case | End Use Electricity |  |  |  |  |  | Savings |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Space Heating [kWh/year] | Space Cooling [kWh/year] | Pumps & Aux [kWh/year] | Vent Fans [kWh/year] | HT Pump Supplement [kWh/year] | Total HVAC [kWh/year] | Total Savings [kWh/year] | % |
| LL51 Baseline Renovated HVAC | 267,720 | 158,213 | 4,125 | 176,143 | 3,896 | 610,097 |  |  |
| Design Case Renovated HVAC | 187,001 | 116,136 | 24,533 | 211,009 | 4 | 538,683 | 71,414 | 11.7% |

# Existing Building Model

  - Describe existing building baseline modeling.

  - Building general description:

  - Fuel types:

Electricity and natural gas are used.

  - Existing HVAC systems.

The existing HVAC consisted of air handling units, unit ventilators, and fin tube radiators. Unit ventilators are connected to a dual temperature water loop for both heating and cooling. Hot water is provided by gas boilers, and chilled water is provided by an electric chiller. All HVAC systems are being replaced in the proposed design.

  - Site visit details

The envelope is in satisfactory condition. The dual-fuel boilers are capable of burning No. 2 oil and natural gas, but currently only natural gas is being used. School personnel have indicated malfunctioning thermostats. Additionally, air dampers and other control devices have been disconnected and are non-operational.

  - Details differing from SCA templates.

Envelope conditions were modeled based on information from existing drawings. Lighting and equipment power densities were modified per the SCA Modeling Guide for Existing Building Electrification. Temperature setpoints were changed to reflect the malfunctioning thermostats.

  - Utility Bill matching

Utility bill matching was performed for electricity and natural gas. The matching was performed per the SCA eQuest Modeling Guide for Existing Building Electrification and using the SCA Appendix A calculator. It was not possible to match the electric demand. The profile of the modeled electric demand is of a similar shape to the profile from the utility bill, but the modeled demand is slightly higher. Matching the electric demand may require assumptions that deviate far from those specified in the Existing Building Electrification Guide.

# Energy Model Calibration Results

3.1 Statistical Analysis:

The CVRMSE and NMBE are referenced in Section 10.2.2 of the SCA eQuest Modeling Guide for Existing Building Electrification.

3.2 Electric Consumption:

3.3 Gas Consumption:

# Proposed Design Modeling Approach.

| EEM Number and Description | Existing Building | Proposed Design | LL51 Baseline |
| --- | --- | --- | --- |
| EEM1: Window Replacements | Existing Windows U-1.25, SHGC-0.82 | New Windows U-0.25, SHGC-0.36 | Identical to Proposed Design |
| EEM2: Lighting Upgrades and Kitchen Electrification | Fluorescent Lighting and Gas Kitchen | LED lighting with lower LPDs in the kitchen, cafeteria, mechanical rooms, and two classrooms. The kitchen is fully electric. | Identical to Proposed Design |
| EEM3: Heating Plant Electrification | 2 Gas Boilers, 80% efficiency 2 Reciprocating Chillers, 2.7 COP | 2 Electric Boilers, 99% efficiency 2 Heat Pump Chillers, 9.63 EER | No Boilers No Chillers |
| EEM4: HVAC System Replacements | Existing AHUs, Unit Ventilators, and Fin Tube Radiators | All existing HVAC is replaced. The AHU condensing units have a higher efficiency and unit ventilators are served by the heat pump chiller. | System 3: Packaged VAV with parallel fan power boxes System 9: Packaged rooftop heat pump |
| EEM5: DHW Heat Pumps | Gas Water Heaters | Heat Pump Water Heaters | Identical to Proposed Design |

# Estimating Savings from EEMs

# Comparison of Existing and Proposed Building

# Appendix A: Side-by-side comparison

| Existing Building Baseline | Proposed Design | LL51 Baseline |
| --- | --- | --- |
| Above grade walls Brick at Full Height: U-0.133 average Face Brick Air Space 1-1/2” Rigid XPS Insulation (R-5/inch) 6” CMU, Solid-Grouted | Above grade walls Identical to Existing Building Baseline | Above grade walls Identical to Existing Building Baseline |
| Below grade walls Foundation Wall: C-0.096 Concrete 1-1/2” Rigid XPS Insulation (R-5/inch) Air Space 4” CMU, Partially-Grouted | Below grade walls Identical to Existing Building Baseline | Below grade walls Identical to Existing Building Baseline |
| Slab on Grade Floors Slab on Grade: F-0.73 Damp Soil Concrete | Slab on Grade Floors Identical to Existing Building Baseline | Slab on Grade Floors Identical to Existing Building Baseline |
| Roof Built-Up Roof: U-0.138 average Gravel Ballast 5” Rigid XPS Insulation (R-5/inch) Concrete Slab on Steel Decking Concrete Slab on Steel Decking Uninsulated parapet (U-1.282) | Roof Identical to Existing Building Baseline | Roof Identical to Existing Building Baseline |
| Vertical fenestration WWR: 17% Assuming ASHRAE A8.2 All Frame Types, Single Glazing U-1.25 SHGC-0.82 | Vertical fenestration WWR: 17% U-0.45 SHGC-0.40 | Vertical fenestration Identical to Proposed Design |
| Doors Swinging Door: U-0.7 | Doors Identical to Existing Building Baseline | Doors Identical to Existing Building Baseline |
| Lighting Power Density Zone Type; W/ft2. Auditorium; 1.58. Cafeteria; 1.33. Classroom; 1.13. Community; 1.75. Conference; 0.70. Copy; 1.25. Corridor; 1.32. IDF/MDF; 0.66. Electrical Room; 0.98. Elevator Lobby; 0.52. Gymnasium; 1.88. Kitchen; 2.00. Library; 2.00. Locker; 1.13. Lounge; 1.10. Mechanical Room; 0.90. Media Room; 1.85. Nurse; 2.00. Office; 0.86. Records; 2.00. Restroom; 1.51. Stair; 1.00. Storage; 0.92. Vestibule; 1.45. | Lighting Power Density Zone Type; W/ft2. Auditorium; 1.58. Cafeteria; 0.26. Classroom; 1.05. Community; 0.49. Conference; 0.70. Copy; 1.25. Corridor; 0.47. IDF/MDF; 0.66. Electrical Room; 0.98. Elevator Lobby; 0.52. Gymnasium; 1.88. Kitchen; 0.61. Library; 2.00. Locker; 0.93. Lounge; 0.39. Mechanical Room; 0.40. Media Room; 1.85. Nurse; 0.75. Office; 0.66. Records; 2.00. Restroom; 1.50. Stair; 1.00. Storage; 0.91. Vestibule; 1.45. | Lighting Power Density Identical to Proposed Design |
| Equipment Power Density Zone Type; W/ft2. Auditorium; 0.66. Cafeteria; 0.25. Classroom; 1.67. Community; 1.96. Conference; 1.96. Copy; 2.87. Corridor; 0.00. IDF/MDF; 28.1. Electrical Room; 0.00. Elevator Lobby; 0.00. Gymnasium; 0.00. Kitchen; 10.81. Library; 0.50. Locker; 0.00. Lounge; 1.96. Mechanical Room; 0.00. Media Room; 1.25. Nurse; 9.07. Office; 4.32. Records; 0.00. Restroom; 0.00. Stair; 0.00. Storage; 1.81. Vestibule; 0.00. | Equipment Power Density Identical to Existing Building Baseline | Equipment Power Density Identical to Existing Building Baseline |

| HVAC equipment |  |  |
| --- | --- | --- |
| Existing Building Baseline | Proposed Design | LL51 Baseline |
| Classroom Systems Unit Ventilators - Dual temperature water loop for both heating and cooling - Constant volume fan control - No energy recovery Unit; Supply CFM; Outside Air CFM; Fan kW. UV-A; 750; 195; 0.087. UV-B; 1,000; 555; 0.087. UV-C; 1,250; 555; 0.087. UV-D; 1,500; 555; 0.087. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). UV-A; 20; 18.9. UV-B; 53.3; 51.8. UV-C; 57.9; 54.3. UV-D; 63.0; 55.3. Air Handling Unit serving 5th Floor Classrooms - DX Cooling Coil - Hot Water Heating Coil - Constant volume fan control assumed due to disconnected dampers - No energy recovery - Cooling Efficiencies assumed based on ASHRAE 90.1-1999 Table 6.2.1A - Cooling Efficiency: 8.9 EER, 7.5 IEER Unit; Supply CFM; Outside Air CFM. AHU-8; 14,900; 3,235. Unit; Supply Fan kW; Return Fan kW. AHU-8; 13.6; 7.24. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-8; 487; 299. Offices and Staff Systems Air Handling Units - DX Cooling Coil - Hot Water Heating Coil - Constant volume fan control assumed due to disconnected dampers - No energy recovery - Cooling Efficiencies assumed based on ASHRAE 90.1-1999 Table 6.2.1A - Cooling Efficiency: 8.9 EER, 7.5 IEER Unit; Supply CFM; Outside Air CFM. AHU-4; 7,500; 2,700. AHU-6; 13,570; 825. AHU-7; 12,000; 1,000. AHU-10; 7,770; 2,270. Unit; Supply Fan kW; Return Fan kW. AHU-4; 6.35; 2.10. AHU-6; 11.6; 6.64. AHU-7; 11.2; 5.53. AHU-10; 7.22; 2.56. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-4; 289; 192. AHU-6; 406; 169. AHU-7; 373; 105. AHU-10; 295; 278. Cellar System serving Electrical/Mechanical and Storage Rooms Air Handling Unit - No Cooling - Hot Water Heating Coil - Constant volume fan control - No energy recovery Unit; Supply CFM; Outside Air CFM; Supply Fan kW. AHU-5; 3,000; 3,000; 1.92. Unit; Heating Capacity (MBH). AHU-5; 227. Gymnasium System Air Handling Unit - DX Cooling Coil - Hot Water Heating Coil - Constant volume fan control assumed due to disconnected dampers - No energy recovery - Cooling Efficiencies assumed based on ASHRAE 90.1-1999 Table 6.2.1A - Cooling Efficiency: 8.9 EER, 7.5 IEER Unit; Supply CFM; Outside Air CFM; Supply Fan kW. AHU-1; 3,200; 1,500; 2.08. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-1; 167; 170. Auditorium System Air Handling Unit - DX Cooling Coil - Hot Water Heating Coil - Constant volume fan control assumed due to disconnected dampers - No energy recovery - Cooling Efficiencies assumed based on ASHRAE 90.1-1999 Table 6.2.1A - Cooling Efficiency: 8.9 EER, 7.5 IEER Unit; Supply CFM; Outside Air CFM. AHU-2; 8,785; 6,000. Unit; Supply Fan kW; Return Fan kW. AHU-2; 6.26; 3.75. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-2; 493; 532. Kitchen/Cafeteria System(s) Cafeteria Air Handling Unit - DX Cooling Coil - Hot Water Heating Coil - Constant volume fan control assumed due to disconnected dampers - No energy recovery - Cooling Efficiencies assumed based on ASHRAE 90.1-1999 Table 6.2.1A - Cooling Efficiency: 8.9 EER, 7.5 IEER Unit; Supply CFM; Outside Air CFM; Supply Fan kW. AHU-3; 7,545; 5,250; 4.75. Unit; Supply Fan kW; Return Fan kW. AHU-3; 4.75; No return fan. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-3; 417; 419. Kitchen Makeup Air Unit - No Cooling - Hot Water Heating Coil - Constant volume fan control - No energy recovery Unit; Supply CFM; Outside Air CFM; Supply Fan kW. AHU-9; 3,300; 3,300; 2.17. Unit; Heating Capacity (MBH). AHU-9; 250. IDF/EMR Room Systems Split AC Unit - DX Cooling Coil - Heat Pump Heating - No outside air - Constant volume fan control - No energy recovery Unit; Supply CFM; Supply Fan kW. AC-3; 205; 0.174. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AC-3; 16.1; 9.2. Heating/Ventilation Systems Hot Water Unit Heaters - Serving mechanical rooms - Hot Water Heating Coils - No outside air - Constant volume fan control Unit; Heating Capacity (MBH). UH-1; 85. UH-2; 40. UH-3; 30. UH-4; 75. UH-5; 115. UH-6; 32. UH-7; 27. UH-8; 32. UH-9; 32. Fin Tube Radiators - Serving corridors, mechanical rooms, offices and the cafeteria - Hot Water Heating - Heating Capacity: 740 Btu/hr per LF | Classroom Systems Unit Ventilators - Dual temperature water loop for both heating and cooling - Constant volume fan control - No energy recovery Unit; Supply CFM; Outside Air CFM; Fan kW. UV-A; 750; 195; 0.235. UV-B; 1,000; 555; 0.276. UV-C; 1,250; 555; 0.327. UV-D; 1,500; 555; 0.327. Unit; Cooling Capacity (kBtu/hr); Heating Capacity (kBtu/hr). UV-A; 31.5; 37.2. UV-B; 40.5; 52.1. UV-C; 53.1; 66.6. UV-D; 53.1; 80.0. Air Handling Unit serving 5th Floor Classrooms - DX Cooling Coil - Heat Pump and Electric Resistance Heating - Variable volume fan control - No energy recovery - Demand control ventilation - Cooling Efficiency: 11.5 EER, 21.5 IEER - Heating Efficiency: 3.6 COP Unit; Supply CFM; Outside Air CFM. AHU-8; 14,900; 3,250. Unit; Supply Fan kW; Return Fan kW. AHU-8; 12.6; No return fan. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-8; 455; 372. Offices and Staff Systems Air Handling Units - DX Cooling Coil - Heat Pump and Electric Resistance Heating - Variable volume fan control - Energy recovery on AHU-4, 77% effectiveness - Energy recovery on AHU-10, 79% effectiveness - Demand control ventilation Unit; Supply CFM; Outside Air CFM. AHU-4; 7,500; 2,700. AHU-6; 13,600; 3,400. AHU-7; 12,000; 3,000. AHU-10; 7,800; 2,270. Unit; Supply Fan kW; Return Fan kW. AHU-4; 7.06; 5.54. AHU-6; 11.2; No return fan. AHU-7; 9.63; No return fan. AHU-10; 7.39; 5.49. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-4; 254; 121. AHU-6; 514; 389. AHU-7; 455; 345. AHU-10; 256; 97. Outdoor Condensing Units Unit; EER; IEER; COP. AHU-4; 11.5; 21.5; 3.6. AHU-6; 11.5; 21.5; 3.6. AHU-7; 11.5; 21.5; 3.6. AHU-10; 11.5; 21.5; 3.6. Cellar System serving Electrical/Mechanical and Storage Rooms Air Handling Unit - DX Cooling Coil - Heat Pump and Electric Resistance Heating - Constant volume fan control - No energy recovery - Demand control ventilation - Cooling Efficiency: 12.5 EER, 24.6 IEER Unit; Supply CFM; Outside Air CFM; Supply Fan kW. AHU-5; 3,000; 3,000; 2.62. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-5; 120; 246. Gymnasium System Air Handling Unit - DX Cooling Coil - Heat Pump and Electric Resistance Heating - Variable volume fan control - No energy recovery - Demand control ventilation - Cooling Efficiency: 12.1 EER, 23 IEER - Heating Efficiency: 3.8 COP Unit; Supply CFM; Outside Air CFM; Supply Fan kW. AHU-1; 3,200; 1,500; 2.73. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-1; 142; 194. Auditorium System Air Handling Unit - DX Cooling Coil - Heat Pump and Electric Resistance Heating - Variable volume fan control - Energy recovery, 73% effectiveness - Demand control ventilation - Cooling Efficiency: 11.1 EER, 21.9 IEER - Heating Efficiency: 3.6 COP Unit; Supply CFM; Outside Air CFM. AHU-2; 8,800; 6,000. Unit; Supply Fan kW; Return Fan kW. AHU-2; 8.28; 6.32. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-2; 329; 387. Kitchen/Cafeteria System(s) Kitchen/Cafeteria Air Handling Unit - DX Cooling Coil - Heat Pump and Electric Resistance Heating - Variable volume fan control - Energy recovery, 75% effectiveness - Demand control ventilation - Cooling Efficiency: 12.1 EER, 23 IEER - Heating Efficiency: 3.8 COP Unit; Supply CFM; Outside Air CFM. AHU-3; 7,600; 5,250. Unit; Supply Fan kW; Return Fan kW. AHU-3; 7.08; 5.68. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-3; 283; 247. Kitchen Makeup Air Unit - AHU-9 removed - The kitchen is served by AHU-2 IDF/EMR Room Systems Existing Split AC Unit serving telecom space - AC-3 removed - The telecom space is now served by AHU-5 New Split AC Units - DX Cooling Coil - Heat Pump Heating - No outside air - Constant volume fan control - No energy recovery Unit; Supply CFM; Supply Fan kW. AC-E1; 661; 0.056. AC-E2; 661; 0.056. HP-1; 581; 0.056. HP-2; 581; 0.056. HP-3; 399; 0.030. AC-5; 215; 0.046. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AC-E1; 22.5; n/a. AC-E2; 22.5; n/a. HP-1; 18.0; 21.6. HP-2; 18.0; 21.6. HP-3; 12.0; 9.79. AC-5; 12.0; n/a. Unit; SEER2; COP. AC-E1; 23.0; n/a. AC-E2; 23.0; n/a. HP-1; 23.0; 2.5. HP-2; 23.0; 2.5. HP-3; 23.0; 2.5. AC-5; 21.0; n/a. Heating/Ventilation Systems - Unit heaters and fin tube radiators will be replaced, but have not yet been specified on mechanical schedules Fin Tube Radiators - Serving corridors, mechanical rooms, offices and the cafeteria - Hot Water Heating - Heating Capacity: 1080 – 1220 Btu/hr per LF Hot Water Convectors - Serving toilets, stairs, storage rooms - Hot Water Heating Electric Unit Heaters - Serving mechanical and storage rooms - Electric Resistance Heating Unit; Supply CFM; Heating Capacity (kW). EUH-1; 2,100; 25. EUH-2; 2,100; 25. EUH-3; 350; 3. EUH-4; 350; 3. | Classroom Systems System 9: Packaged Rooftop Heat Pump - DX Cooling Coil - Heat Pump Heating - Cooling Efficiency: 14 SEER - Heating Efficiency: 8 HSPF System 3: Packaged VAV with Parallel Fan-Powered Boxes - DX Cooling Coil - Electric Resistance Heating - Variable volume fan control - No energy recovery - Demand control ventilation - Cooling Efficiency: 10 EER, 11.6 IEER Unit; Supply CFM; Outside Air CFM. AHU-8; 15,131; 3,223. Unit; Supply Fan kW; Return Fan kW. AHU-8; 13.1; No return fan. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-8; 471; 569. Offices and Staff Systems System 3: Packaged VAV with Parallel Fan-Powered Boxes - DX Cooling Coil - Electric Resistance Heating - Variable volume fan control - Energy recovery on AHU-4 and AHU-10, 50% effectiveness - Demand control ventilation Unit; Supply CFM; Outside Air CFM. AHU-4; 8,518; 2,700. AHU-6; 12,865; 3,383. AHU-7; 11,683; 3,003. AHU-10; 7,889; 2,272. Unit; Supply Fan kW; Return Fan kW. AHU-4; 7.25; 6.44. AHU-6; 10.8; No return fan. AHU-7; 9.58; No return fan. AHU-10; 7.15; 5.32. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-4; 280; 161. AHU-6; 498; 514. AHU-7; 446; 473. AHU-10; 253; 122. Cooling Efficiency Unit; EER; IEER. AHU-4; 11; 12.4. AHU-6; 10; 11.6. AHU-7; 10; 11.6. AHU-10; 10; 11.6. Cellar System serving Electrical/Mechanical and Storage Rooms System 3: Packaged VAV with Parallel Fan-Powered Boxes - DX Cooling Coil - Electric Resistance Heating - Constant volume fan control - No energy recovery - Demand control ventilation - Cooling Efficiency: 11.2 EER, 12.9 IEER Unit; Supply CFM; Outside Air CFM; Supply Fan kW. AHU-5; 3,015; 3,015; 2.69. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-5; 121; 247. Gymnasium System System 9: Packaged Rooftop Heat Pump - DX Cooling Coil - Heat Pump Heating - Two-speed fan control - No energy recovery - Demand control ventilation - Cooling Efficiency: 10.4 EER, 11.4 IEER - Heating Efficiency: 3.2 COP Unit; Supply CFM; Outside Air CFM; Supply Fan kW. AHU-1; 3,197; 1,499; 2.79. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-1; 143; 194. Auditorium System System 9: Packaged Rooftop Heat Pump - DX Cooling Coil - Heat Pump Heating - Two-speed fan control - Energy recovery, 50% effectiveness - Demand control ventilation - Cooling Efficiency: 9.3 EER, 10.4 IEER - Heating Efficiency: 3.2 COP Unit; Supply CFM; Outside Air CFM. AHU-2; 8,878; 6,002. Unit; Supply Fan kW; Return Fan kW. AHU-2; 7.96; 6.07. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-2; 329; 389. Kitchen/Cafeteria System(s) System 9: Packaged Rooftop Heat Pump - DX Cooling Coil - Heat Pump Heating - Two-speed fan control - Energy recovery, 50% effectiveness - Demand control ventilation - Cooling Efficiency: 9.3 EER, 10.4 IEER - Heating Efficiency: 3.2 COP Unit; Supply CFM; Outside Air CFM. AHU-3; 7,632; 5,243. Unit; Supply Fan kW; Return Fan kW. AHU-3; 6.69; 5.38. Unit; Cooling Capacity (MBH); Heating Capacity (MBH). AHU-3; 282; 247. Kitchen Makeup Air Unit - No unit modeled IDF/EMR Room Systems System 9: Packaged Rooftop Heat Pump - DX Cooling Coil - Heat Pump Heating - No outside air - Two-speed fan control - No energy recovery System; Supply CFM; Supply Fan kW. AC-E1-E2-HP-3; 1,721; 0.142. HP-1-2; 1,162; 0.136. AC-5; 549; 0.142. System; Cooling Capacity (MBH); Heating Capacity (MBH). AC-E1-E2-HP-3; 57; 9.79. HP-1-2; 36.1; 76.8. AC-5; 18.64; n/a. System; SEER; HSPF. AC-E1-E2-HP-3; 14; 8. HP-1-2; 14; 8. AC-5; 14; 8. Heating/Ventilation Systems System 9: Packaged Rooftop Heat Pump - DX Cooling Coil - Heat Pump Heating - No outside air - Two-speed fan control - No energy recovery - Cooling Efficiency: 14 SEER - Heating Efficiency: 8 HSPF |
| Heating plant |  |  |
| Existing Building Baseline 2 Natural Gas Boilers - 5,021 kBtu/hr each - 80% thermal efficiency 1 Primary Boiler Pumps (plus 1 standby) - 518 GPM each - 11.2 kW each 1 Secondary Boiler Pumps (plus 1 standby) for Perimeter Heating - 50 GPM each - 1.6 kW each | Proposed Design 2 Electric Boilers - 478 kBtu/hr each - 99% thermal efficiency 1 Primary Hot Water Pump (plus 1 standby) for Perimeter Heating - 50 GPM each - 1.4 kW each | LL51 Baseline No heating plant |
| Cooling plant |  |  |
| Existing Building Baseline 2 Reciprocating Air Cooled Chillers - 100 tons each - 2.7 COP per ASHRAE 90.1-1999 Table 6.2.1C 2 Primary Chiller Pumps (plus 1 standby) - 200 GPM each - 4.0 kW each 1 Dual Temperature Water Pumps (plus 1 standby) - 312 GPM each - 7.4 kW each | Proposed Design 2 Heat Pump Chillers - Cooling Capacity: 1,378 kBtu/hr - Heating Capacity: 1,445 kBtu/hr - Cooling Efficiency: 9.63 EER, 13.14 IEER - Heating Efficiency: 3.15 COP 2 Dual Temperature Water Pumps (plus 1 standby) - 280 GPM each - 5.9 kW each | LL51 Baseline No cooling plant |
| Domestic hot water heating |  |  |
| Existing Building Baseline 2 Gas Hot Water Heaters - Capacity: 500 kBtu/hr each - 65% thermal efficiency - One 74 gallon tank each (148 gallons total) | Proposed Design 2 Heat Pump Water Heaters - Capacity: 108 kBtu/hr each - 2.04 COP - One 150 gallon tank for both units | LL51 Baseline Identical to Proposed Design |

# Appendix B: Energy Model Outputs  - Existing Building TMY3 with Current Utility Rates

Existing Building Baseline

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024     9:39:14  BDL RUN  7

EXISTING BUILDING MODEL w/ STD WEATHER

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       248315.    2431.  376338.       0.  351909.       0.   19478.  496891.       0.       0.       0.   12473.  1507838.

MF-M NATURAL-GAS

THERM          0.       0.     790.   35938.       0.       0.       0.       0.       0.       0.    6113.       0.    42840.

TOTAL ELECTRICITY   1507838. KWH        13.128 KWH     /SQFT-YR GROSS-AREA   13.128 KWH     /SQFT-YR NET-AREA

TOTAL NATURAL-GAS     42840. THERM       0.373 THERM   /SQFT-YR GROSS-AREA    0.373 THERM   /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE = 72.36

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  0.00

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =  5870

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =   895

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024     9:39:14  BDL RUN  7

EXISTING BUILDING MODEL w/ STD WEATHER

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1507838. KWH           313173.       0.2077      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M              42840. THERM          53360.       1.2456      YES

==========

366533.

ENERGY COST/GROSS BLDG AREA:      3.19

ENERGY COST/NET BLDG AREA:      3.19

Proposed Design

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    15:13:54  BDL RUN  5

DHW AND OTHER MEASURES

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       213391.    2431.  389412.  264170.  116450.       0.   20466.  205659.       0.       3.   21314.   12473.  1245772.

MF-M NATURAL-GAS

THERM          0.       0.       0.       0.       0.       0.       0.       0.       0.       0.       0.       0.        0.

TOTAL ELECTRICITY   1245772. KWH        10.846 KWH     /SQFT-YR GROSS-AREA   10.846 KWH     /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE =  3.15

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  6.76

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =   141

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =   135

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    15:13:54  BDL RUN  5

DHW AND OTHER MEASURES

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1245772. KWH           361334.       0.2900      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M                  0. THERM              0.       0.0000      YES

==========

361334.

ENERGY COST/GROSS BLDG AREA:      3.15

ENERGY COST/NET BLDG AREA:      3.15

LL51 Baseline

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    12:35:41  BDL RUN  4

ASH90.1-2016 NYC ECB MODEL

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       215015.    2453.  391576.  347701.  150672.       0.    4119.  176176.       0.    5614.   21332.   12473.  1327134.

MF-M NATURAL-GAS

THERM          0.       0.       0.       0.       0.       0.       0.       0.       0.       0.       0.       0.        0.

TOTAL ELECTRICITY   1327134. KWH        11.554 KWH     /SQFT-YR GROSS-AREA   11.554 KWH     /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE =  3.23

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  0.02

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =    87

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =   196

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    12:35:41  BDL RUN  4

ASH90.1-2016 NYC ECB MODEL

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1327134. KWH           373610.       0.2815      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M                  0. THERM              0.       0.0000      YES

==========

373610.

ENERGY COST/GROSS BLDG AREA:      3.25

ENERGY COST/NET BLDG AREA:      3.25

EEM 1: Window Replacements

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024     9:23:40  BDL RUN  2

ENVELOPE MEASURES

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       248315.    2431.  376338.       0.  349040.       0.   17866.  505273.       0.       0.       0.   12473.  1511739.

MF-M NATURAL-GAS

THERM          0.       0.     790.   25258.       0.       0.       0.       0.       0.       0.    6113.       0.    32161.

TOTAL ELECTRICITY   1511739. KWH        13.162 KWH     /SQFT-YR GROSS-AREA   13.162 KWH     /SQFT-YR NET-AREA

TOTAL NATURAL-GAS     32161. THERM       0.280 THERM   /SQFT-YR GROSS-AREA    0.280 THERM   /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE = 77.19

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  0.00

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =  6529

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =   432

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024     9:23:40  BDL RUN  2

ENVELOPE MEASURES

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1511739. KWH           310055.       0.2051      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M              32161. THERM          39994.       1.2436      YES

==========

350049.

ENERGY COST/GROSS BLDG AREA:      3.05

ENERGY COST/NET BLDG AREA:      3.05

EEM 2: Lighting Upgrades and Kitchen Electrification

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024     9:28:19  BDL RUN  3

INTERIOR LOAD MEASURES

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       213391.    2431.  389412.       0.  342982.       0.   17876.  497544.       0.       0.       0.   12473.  1476111.

MF-M NATURAL-GAS

THERM          0.       0.       0.   24943.       0.       0.       0.       0.       0.       0.    6113.       0.    31056.

TOTAL ELECTRICITY   1476111. KWH        12.851 KWH     /SQFT-YR GROSS-AREA   12.851 KWH     /SQFT-YR NET-AREA

TOTAL NATURAL-GAS     31056. THERM       0.270 THERM   /SQFT-YR GROSS-AREA    0.270 THERM   /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE = 74.71

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  0.00

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =  6300

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =   454

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024     9:28:19  BDL RUN  3

INTERIOR LOAD MEASURES

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1476111. KWH           301940.       0.2046      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M              31056. THERM          38572.       1.2420      YES

==========

340512.

ENERGY COST/GROSS BLDG AREA:      2.96

ENERGY COST/NET BLDG AREA:      2.96

EEM 3: Heating Plant Electrification

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    17:30:45  BDL RUN  6

HEATING PLANT MEASURES

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       213391.    2431.  389412.  408378.  314257.       0.   19099.  507322.       0.       0.       0.   12473.  1866767.

MF-M NATURAL-GAS

THERM          0.       0.       0.       0.       0.       0.       0.       0.       0.       0.    6113.       0.     6113.

TOTAL ELECTRICITY   1866767. KWH        16.253 KWH     /SQFT-YR GROSS-AREA   16.253 KWH     /SQFT-YR NET-AREA

TOTAL NATURAL-GAS      6113. THERM       0.053 THERM   /SQFT-YR GROSS-AREA    0.053 THERM   /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE = 76.76

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  4.61

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =  6261

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =  2275

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    17:30:45  BDL RUN  6

HEATING PLANT MEASURES

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1866767. KWH           444301.       0.2380      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M               6113. THERM           8067.       1.3197      YES

==========

452368.

ENERGY COST/GROSS BLDG AREA:      3.94

ENERGY COST/NET BLDG AREA:      3.94

EEM 4: HVAC System Replacements

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    17:51:56  BDL RUN  7

ALL HVAC MEASURES

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       213391.    2431.  389412.  264170.  116450.       0.   20466.  205659.       0.       3.       0.   12473.  1224458.

MF-M NATURAL-GAS

THERM          0.       0.       0.       0.       0.       0.       0.       0.       0.       0.    6113.       0.     6113.

TOTAL ELECTRICITY   1224458. KWH        10.660 KWH     /SQFT-YR GROSS-AREA   10.660 KWH     /SQFT-YR NET-AREA

TOTAL NATURAL-GAS      6113. THERM       0.053 THERM   /SQFT-YR GROSS-AREA    0.053 THERM   /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE =  3.15

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  6.76

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =   141

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =   135

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    17:51:56  BDL RUN  7

ALL HVAC MEASURES

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1224458. KWH           357618.       0.2921      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M               6113. THERM           8067.       1.3197      YES

==========

365684.

ENERGY COST/GROSS BLDG AREA:      3.18

ENERGY COST/NET BLDG AREA:      3.18

EEM 5: DHW Heat Pumps

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    15:13:54  BDL RUN  5

DHW AND OTHER MEASURES

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       213391.    2431.  389412.  264170.  116450.       0.   20466.  205659.       0.       3.   21314.   12473.  1245772.

MF-M NATURAL-GAS

THERM          0.       0.       0.       0.       0.       0.       0.       0.       0.       0.       0.       0.        0.

TOTAL ELECTRICITY   1245772. KWH        10.846 KWH     /SQFT-YR GROSS-AREA   10.846 KWH     /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE =  3.15

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  6.76

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =   141

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =   135

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024    15:13:54  BDL RUN  5

DHW AND OTHER MEASURES

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- NEW YORK CENTRAL  NY

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1245772. KWH           361334.       0.2900      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M                  0. THERM              0.       0.0000      YES

==========

361334.

ENERGY COST/GROSS BLDG AREA:      3.15

ENERGY COST/NET BLDG AREA:      3.15

Utility Matched Model

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024     9:42:57  BDL RUN  8

EXISTING BUILDING MODEL

REPORT- BEPU Building Utility Performance                                                   WEATHER FILE- EPW NYC-CENTRAL-PARK

---------------------------------------------------------------------------------------------------------------------------------

TASK     MISC    SPACE    SPACE     HEAT    PUMPS     VENT    REFRIG  HT PUMP   DOMEST    EXT

LIGHTS   LIGHTS   EQUIP   HEATING  COOLING   REJECT   & AUX     FANS   DISPLAY  SUPPLEM  HOT WTR   USAGE    TOTAL

-------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  -------  --------

ME-M ELECTRICITY

KWH       250171.    2453.  378475.       0.  363829.       0.   18260.  500821.       0.       0.       0.   12473.  1526483.

MF-M NATURAL-GAS

THERM          0.       0.     796.   28259.       0.       0.       0.       0.       0.       0.    6062.       0.    35117.

TOTAL ELECTRICITY   1526483. KWH        13.290 KWH     /SQFT-YR GROSS-AREA   13.290 KWH     /SQFT-YR NET-AREA

TOTAL NATURAL-GAS     35117. THERM       0.306 THERM   /SQFT-YR GROSS-AREA    0.306 THERM   /SQFT-YR NET-AREA

PERCENT OF HOURS ANY SYSTEM ZONE OUTSIDE OF THROTTLING RANGE = 74.63

PERCENT OF HOURS ANY PLANT LOAD NOT SATISFIED                =  0.00

HOURS ANY ZONE ABOVE COOLING THROTTLING RANGE                =  6256

HOURS ANY ZONE BELOW HEATING THROTTLING RANGE                =   478

NOTE:  ENERGY IS APPORTIONED HOURLY TO ALL END-USE CATEGORIES.

DOE 2.2                                 MEDIUM SCHOOL TEMPLATE                  DOE-2.2-50a    3/28/2024     9:42:57  BDL RUN  8

EXISTING BUILDING MODEL

REPORT- ES-D Energy Cost Summary                                                            WEATHER FILE- EPW NYC-CENTRAL-PARK

---------------------------------------------------------------------------------------------------------------------------------

METERED             TOTAL      VIRTUAL

ENERGY            CHARGE         RATE   RATE USED

UTILITY-RATE                       RESOURCE           METERS              UNITS/YR               ($)     ($/UNIT)   ALL YEAR?

--------------------------------   ----------------   -----------   -------------------   ----------   ----------   ---------

REG-ELEC-TARIFF                    ELECTRICITY        ME-M            1526483. KWH           310267.       0.2033      YES

REG-GAS-TARIFF                     NATURAL-GAS        MF-M              35117. THERM          43795.       1.2471      YES

==========

354062.

ENERGY COST/GROSS BLDG AREA:      3.08

ENERGY COST/NET BLDG AREA:      3.08