## General Information
School Name
Model Submission
Drawing Set
GSG Baseline | 2019 GSG- ASHRAE 90.1-2010
LL32 Baseline | NYC ECC 2020 Energy Cost Budget

## Envelope
F-Factor Calculations for Slab-On-Grade
Unheated Slab Area | 5000 | ft2
Unheated Slab Perimeter | 300 | ft
Heated Slab Area | 5000 | ft2
Heated Slab Perimeter | 300 | ft
Material | R-Value (eQuest Input) | F-Factor (Btu/hr-ft-F | Heat Transferred (Btu/hr-F) | Slab Cons. U-value | Description
UFMAT-UH-PROP | 54.1556 | 0.3 | 90 | 0.018 | Proposed Design, unheated slab
UFMAT-UH-NYC20 | 30.6513 | 0.52 | 156 | 0.0312 | LL32 Baseline per NYCECC 2020, unheated slab
UFMAT-UH-ASH10 | 21.4311 | 0.73 | 219 | 0.0438 | GSG 2019 Baseline, unheated slab
UFMAT-HT-PROP | 36.4788 | 0.44 | 132 | 0.0264 | Proposed Design, heated slab
UFMAT-HT-NYC20 | 25.055 | 0.63 | 189 | 0.0378 | LL32 Baseline per NYCECC 2020, heated slab
UFMAT-HT-ASH10 | 17.9798 | 0.86 | 258 | 0.0516 | GSG 2019 Baseline, heated slab
Window Calculations for Project Specific Windows
Copy rows for additional windows as needed
Glass-Type Name (eQuest Input) | Assembly U-Value, Actual (Btu/ft2-F-hr) | SHGC | Glass Conductance (eQuest Input) | Shading Coefficient (eQuest Input)
Sample Win | 0.31 | 0.27 | 0.32725 | 0.31395
Window U-Value Calculations for Combined Fixed & Operable Units
Applies to metal framed windows only. Curtainwall and storefront windows should be modeled separately.
[5 empty] | Average Assembly U Values, Actual (BTU/hr-ft2-F) |  |  | eQuest Glass-Conductance Input Values
Glass-Type Name (eQuest Input) | Fixed Area (% or ft2) | Operable Area (% or ft2) | Proposed Fixed Assembly U-Value, Actual (Btu/ft2-F-hr) | Proposed Operable Assembly U-Value, Actual (Btu/ft2-F-hr) | Proposed | LL32 Glass Conductance (Actual Average) | GSG Baseline Glass Conductance (eQuest Input) | Proposed Glass Conductance (eQuest Input) | LL32 Glass Conductance (eQuest Input) | GSG Baseline Glass Conductance (eQuest Input) | LL32 Fixed U | LL32 Operable U | GSG Fixed U | GSG Operable U
Sample Win | 0.66 | 0.33 | 0.31 | 0.6 | 0.40667 | 0.33333 | 0.45 | 0.43687 | 0.35336 | 0.48728 | 0.3 | 0.4 | 0.4 | 0.55
[11 empty] | 0.3 | 0.4 | 0.4 | 0.55
[11 empty] | 0.3 | 0.4 | 0.4 | 0.55
[11 empty] | 0.3 | 0.4 | 0.4 | 0.55
[11 empty] | 0.3 | 0.4 | 0.4 | 0.55
[11 empty] | 0.3 | 0.4 | 0.4 | 0.55
[11 empty] | 0.3 | 0.4 | 0.4 | 0.55

## Gym occupancy
Gym area | 2500 | ft2 | Provide Area
Area/person | 15 |  | Defaults: 21 for Medium school template, 15 for Large school template
Gym population | 166.6667 | people | Override if matching the occupancy in the design documents
Class size | 24 | people
PE class occupancy | 48 | people
Medium school template (PS/ECC) or gyms without bleachers
|  |  | Hour | GYM-OCC-SMR-WD = DAY-SCHEDULE | GYM-OCC-WTR-WD = DAY-SCHEDULE |  | Gym summer occupancy | Gym winter occupancy
|  |  |  | TYPE = FRACTION | TYPE = FRACTION
|  |  |  | (1,24)( | (1,24)( |  | people | people
|  |  | 1 | 0 | 0 |  | 0 | 0
|  |  | 2 | 0 | 0 |  | 0 | 0
|  |  | 3 | 0 | 0 |  | 0 | 0
|  |  | 4 | 0 | 0 |  | 0 | 0
|  |  | 5 | 0 | 0 |  | 0 | 0
|  |  | 6 | 0 | 0 |  | 0 | 0
|  |  | 7 | 0 | 0 |  | 0 | 0
|  |  | 8 | 0 | 0 |  | 0 | 0
|  |  | 9 | 0.144 | 0.288 |  | 24 | 48 |  | Class
|  |  | 10 | 0.144 | 0.288 |  | 24 | 48
|  |  | 11 | 0.144 | 0.288 |  | 24 | 48
|  |  | 12 | 0.144 | 0.288 |  | 24 | 48
|  |  | 13 | 0.144 | 0.288 |  | 24 | 48
|  |  | 14 | 0.144 | 0.288 |  | 24 | 48
|  |  | 15 | 0.144 | 0.288 |  | 24 | 48
|  |  | 16 | 0.144 | 0.144 |  | 24 | 24 |  | Practice
|  |  | 17 | 0 | 0.144 |  | 0 | 24
|  |  | 18 | 0 | 0 |  | 0 | 0
|  |  | 19 | 0 | 0 |  | 0 | 0 |  | Game
|  |  | 20 | 0 | 0 |  | 0 | 0
|  |  | 21 | 0 | 0 |  | 0 | 0
|  |  | 22 | 0 | 0 |  | 0 | 0
|  |  | 23 | 0 | 0 |  | 0 | 0
|  |  | 24 | 0 | 0 |  | 0 | 0
|  |  |  | ) | )
|  |  |  | .. | ..
Large school template (IS/HS) or gyms with bleachers
|  |  | Hour | GYM-OCC-SMR-WD = DAY-SCHEDULE | GYM-OCC-WTR-WD = DAY-SCHEDULE | GYM-EXT-OCC-WED = DAY-SCHEDULE | Gym summer occupancy | Gym winter occupancy | Extended gym occupancy
|  |  |  | TYPE = FRACTION | TYPE = FRACTION | TYPE = FRACTION
|  |  |  | (1,24)( | (1,24)( | (1,24)( | people | people | people
|  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 9 | 0.144 | 0.288 | 0.288 | 24 | 48 | 48 | Class
|  |  | 10 | 0.144 | 0.288 | 0.288 | 24 | 48 | 48
|  |  | 11 | 0.144 | 0.288 | 0.288 | 24 | 48 | 48
|  |  | 12 | 0.144 | 0.288 | 0.288 | 24 | 48 | 48
|  |  | 13 | 0.144 | 0.288 | 0.288 | 24 | 48 | 48
|  |  | 14 | 0.144 | 0.288 | 0.288 | 24 | 48 | 48
|  |  | 15 | 0.144 | 0.288 | 0.288 | 24 | 48 | 48
|  |  | 16 | 0.144 | 0.144 | 0.144 | 24 | 24 | 24 | Practice
|  |  | 17 | 0.144 | 0.144 | 0.144 | 24 | 24 | 24
|  |  | 18 | 0.144 | 0.144 | 0.144 | 24 | 24 | 24
|  |  | 19 | 0.144 | 0 | 1 | 24 | 0 | 166.6667 | Game
|  |  | 20 | 0.144 | 0 | 1 | 24 | 0 | 166.6667
|  |  | 21 | 0.144 | 0 | 1 | 24 | 0 | 166.6667
|  |  | 22 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 24 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | ) | ) | )
|  |  |  | .. | .. | ..

## Air Cooled Chiller Calc
EIR-FT
a | 0.46971
b | -0.0036153
c | 3.854e-05
d | 0.0062869
e | 5.077e-05
f | -0.00010546
Provide all of the manufacturer information in Columns A through D. Additional lines may be added.
Copy the Independent data points from Column A to the eQuest curve
Copy the Dependent data points from Column H to the eQuest curve
PLR | CHWT | DBT | Efficiency (kW/ton) | Energy used @ Load (A x D) | Target E-I-R | EIR-FT | EIR-FPLR
1 | 42 | 95 | 1.298 | 1.298 | 1 | 1.0205 | 0.9799
0.75 | 42 | 85 | 1.025 | 0.76875 | 0.59226 | 0.91056 | 0.65043
0.5 | 42 | 65 | 0.838 | 0.419 | 0.3228 | 0.7211 | 0.44766
0.25 | 42 | 55 | 0.747 | 0.18675 | 0.14388 | 0.6416 | 0.22425
This curve is only valid if the built in curve RecipAir-EIR-fCHWT&DBT is used for the Performance Curve f(t evap leaving, t cond entering)

## Air Cooled DX IEER
The calculations on this spreadsheet will provide the coefficients for the COOL-EIR-FPLR curve that achieve the rated IPLV.
The EER and IEER must be provided at ARI rated conditions.
Provide the Manufacturer's EER & IEER Below
EER | 14.936 | Full Load @ ARI Conditions
IEER | 22 | At ARI Conditions
Full load efficiency | 0.80343 | kW/ton
Full load power | 0.80343 | kW
DEFAULT DOE2 CURVES
DOE Code word | Curve Name | Curve Type | A | B | C | D | E | F | TEST X | TEST Y | RESULT | TARGET
COOL-EIR-FT | DX-Cool-EIR-fEWB&OAT | BI-QUADRATIC-T | -1.0639 | 0.030658 | -0.0001269 | 0.015421 | 4.973e-05 | -0.0002096 | 67 | 95 | 1.0003 | 1
COOL-EIR-FPLR | DX-Cool-EIR-fPLR | cubic | 0.20123 | -0.031217 | 1.9505 | -1.1205 |  |  | 1 |  | 1 | 1
CALCULATIONS
From AHRI Rating Conditions |  |  | Default DOE2 | [6 empty] | INPUT TO DOE2
PLR | EWB | OAT | EIR OAT | EIR PLR | EIR Correction | Load | kW | kW/ton | IEER | Revised EIR PLR | Rev EIR | Revised kW | Rev. kW/ton | Rev IEER
1 | 67 | 95 | 1.0003 | 1 | 1.0003 | 1 | 0.80364 | 0.80364 | 14.9321 | 1 | 1.0003 | 0.80364 | 0.80364 | 14.9321
0.75 | 67 | 81.5 | 0.86316 | 0.80226 | 0.69248 | 0.75 | 0.55636 | 0.74181 | 16.1767 | 0.61756 | 0.53305 | 0.42827 | 0.57103 | 21.0148
0.5 | 67 | 68 | 0.74419 | 0.53318 | 0.39679 | 0.5 | 0.31879 | 0.63758 | 18.821 | 0.41043 | 0.30544 | 0.2454 | 0.4908 | 24.45
0.25 | 67 | 65 | 0.72022 | 0.29782 | 0.2145 | 0.25 | 0.17233 | 0.68933 | 17.4081 | 0.22926 | 0.16511 | 0.13266 | 0.53063 | 22.6146
[7 empty] | IEER | 0.71168 | 16.9351 |  |  |  |  | 21.9107
|  |  | 1.5932 | -2.1821 | 1.6643 | -0.075322
Use the coefficients below for the revised COOL-EIR-FPLR Curve (TYPE = CUBIC)
A | -0.075322
B | 1.6643
C | -2.1821
D | 1.5932
This curve is only valid if the built in curve DX-Cool-EIR-fEWB&OAT is used for the COOL-EIR-FT Performance Curve f(t evap leaving, t cond entering)
This curve can only be used for air-cooled DX systems.

## VRF HP IEER
The calculations on this spreadsheet will provide the coefficients for the COOL-EIR-FPLR curve that achieve the rated IPLV.
The EER and IEER must be provided at ARI rated conditions.
Provide the Manufacturer's EER & IEER Below
EER | 13 | Full Load @ ARI Conditions
IEER | 22 | At ARI Conditions
Full load efficiency | 0.92308 | kW/ton
Full load power | 0.92308 | kW
DEFAULT DOE2 CURVES
DOE Code word | Curve Name | Curve Type | A | B | C | D | E | F | TEST X | TEST Y | RESULT | TARGET
COOL-EIR-FT | VRF Cooling EIR F EWB / ODB | BI-QUADRATIC-T | 1.5657 | -0.02679 | 0.00021 | -0.00566 | 7e-05 | 3e-05 | 67 | 95 | 0.99847 | 1
COOL-EIR-FPLR | VRF Cooling PLR | quadratic | 0.1181 | 0.3937 | 0.4731 | 0 |  |  | 1 |  | 0.9849 | 1
|  | cubic | -0.14875 | 2.0631 | -3.4733 | 2.5589 |  |  | 1 |  | 1 | 1
CALCULATIONS
From AHRI Rating Conditions |  |  | Default DOE2 | [6 empty] | INPUT TO DOE2
PLR | EWB | OAT | EIR OAT | EIR PLR | EIR Correction | Load | kW | kW/ton | IEER | Revised EIR PLR | Rev EIR | Revised kW | Rev. kW/ton | Rev IEER
1 | 67 | 95 | 0.99847 | 0.9849 | 0.98339 | 1 | 0.90775 | 0.90775 | 13.2195 | 1 | 0.99847 | 0.92166 | 0.92166 | 13.0199
0.75 | 67 | 81.5 | 0.88095 | 0.67949 | 0.5986 | 0.75 | 0.55256 | 0.73674 | 16.288 | 0.5244 | 0.46197 | 0.42644 | 0.56858 | 21.1051
0.5 | 67 | 68 | 0.78895 | 0.43323 | 0.34179 | 0.5 | 0.3155 | 0.631 | 19.0174 | 0.33434 | 0.26378 | 0.24349 | 0.48698 | 24.6417
0.25 | 67 | 65 | 0.77197 | 0.24609 | 0.18998 | 0.25 | 0.17536 | 0.70145 | 17.1073 | 0.18992 | 0.14662 | 0.13534 | 0.54135 | 22.1668
[7 empty] | IEER | 0.71058 | 16.9786 |  |  |  |  | 21.9178
|  |  | 2.5589 | -3.4733 | 2.0631 | -0.14875
Use the coefficients below for the revised COOL-EIR-FPLR Curve (TYPE = CUBIC)
A | -0.14875
B | 2.0631
C | -3.4733
D | 2.5589
This curve is only valid if the Mitsubishi curve "VRF Cooling EIR F EWB / ODB" is used for the COOL-EIR-FT Performance Curve f(t evap leaving, t cond entering)
This curve can only be used for air-cooled DX systems.

## VRF HP IEER Daikin (hidden)
The calculations on this spreadsheet will provide the coefficients for the COOL-EIR-FPLR curve that achieve the rated IPLV.
The EER and IEER must be provided at ARI rated conditions.
Provide the Manufacturer's EER & IEER Below
EER | 13 | Full Load @ ARI Conditions
IEER | 22 | At ARI Conditions
Full load efficiency | 0.92308 | kW/ton
Full load power | 0.92308 | kW
DEFAULT DOE2 CURVES
DOE Code word | Curve Name | Curve Type | A | B | C | D | E | F | TEST X | TEST Y | RESULT | TARGET
COOL-EIR-FT | VRVACHP-CoolEIR-fEWB&ODB | BI-QUADRATIC-T | -1.5191 | 0.0683 | -0.0005345 | -0.01715 | 0.0001297 | 0.000119 | 67 | 95 | 0.95639 | 1
COOL-EIR-FPLR | VRVACHP-Cool-PLR | quadratic | 0.076754 | 0.32714 | 0.596 | 0 |  |  | 1 |  | 0.99989 | 1
|  | cubic | 0.067732 | 0.38593 | 0.45688 | 0.089459 |  |  | 1 |  | 1 | 1
CALCULATIONS
From AHRI Rating Conditions |  |  | Default DOE2 | [6 empty] | INPUT TO DOE2
PLR | EWB | OAT | EIR OAT | EIR PLR | EIR Correction | Load | kW | kW/ton | IEER | Revised EIR PLR | Rev EIR | Revised kW | Rev. kW/ton | Rev IEER
1 | 67 | 95 | 0.95639 | 0.99989 | 0.95629 | 1 | 0.88273 | 0.88273 | 13.5942 | 1 | 0.95639 | 0.88282 | 0.88282 | 13.5928
0.75 | 67 | 81.5 | 0.77124 | 0.65736 | 0.50698 | 0.75 | 0.46798 | 0.62398 | 19.2315 | 0.65191 | 0.50278 | 0.46411 | 0.61881 | 19.3921
0.5 | 67 | 68 | 0.63336 | 0.38932 | 0.24658 | 0.5 | 0.22761 | 0.45523 | 26.3603 | 0.3861 | 0.24454 | 0.22573 | 0.45146 | 26.5804
0.25 | 67 | 65 | 0.60914 | 0.19579 | 0.11926 | 0.25 | 0.11009 | 0.44036 | 27.2506 | 0.19417 | 0.11828 | 0.10918 | 0.43671 | 27.4782
[7 empty] | IEER | 0.56604 | 21.8178 |  |  |  |  | 21.9977
|  |  | 0.089459 | 0.45688 | 0.38593 | 0.067732
Use the coefficients below for the revised COOL-EIR-FPLR Curve (TYPE = CUBIC)
A | 0.067732
B | 0.38593
C | 0.45688
D | 0.089459
This curve is only valid if the Mitsubishi curve "VRF Cooling EIR F EWB / ODB" is used for the COOL-EIR-FT Performance Curve f(t evap leaving, t cond entering)
This curve can only be used for air-cooled DX systems.

## Domestic Hot Water
Hot Water Demand Calculations
[5 empty] | Step 1: Insert Occupancy Info | [23 empty] | supply T | 140 | F | [5 empty] | DHW schedule
Hot Water Load Inputs | [13 empty] | Regular |  | Summer | [12 empty] | average ground water temperature | 57 | F | [5 empty] | WD | Toilet | Kitchen | WEH | Toilet | Kitchen |  | Days per Year
[5 empty] | Total number students | [8 empty] | 0 |  | 0 |  | Reference Table 1: Instructional Days | [18 empty] | 1 | 0.01 | 0.05 |  | 0.01 | 0.05 | Holiday | 11 | per equest manual
|  | Regular | Summer |  | Total number of staff | [8 empty] | 0 |  | 0 |  | Annual Instruction Days School is in Full Operation |  |  |  |  | 180 | [13 empty] | 2 | 0.01 | 0.05 |  | 0.01 | 0.05 | Monday | 50
Total number of Students in Project Area |  | 0 | 0 | Information from W2.1P, W2.2R tab in GSG Report | Number of D75 students in classrooms with toilets | [8 empty] | 0 |  | 0 |  | Annual Instructional Days School is in Summer Operation |  |  |  |  | 30 | [13 empty] | 3 | 0.01 | 0.05 |  | 0.01 | 0.05 | Tuesday | 50
Total number of Staff in Project Area |  | 0 | 0 | Information from W2.1P, W2.2R tab in GSG Report | Total students PK to K | [8 empty] | 0 |  | 0 | [20 empty] | 4 | 0.01 | 0.05 |  | 0.01 | 0.05 | Wednesday | 50
Number of D75 students in classrooms with toilets |  | 0 | 0 | Information from W2.1P, W2.2R tab in GSG Report | Conventional Water Closet (male 1-12) | [8 empty] | 0 |  | 0 | [20 empty] | 5 | 0.01 | 0.05 |  | 0.01 | 0.05 | Thursday | 50
Total students PK to K |  | 0 | 0 | Information from W2.1P, W2.2R tab in GSG Report | Conventional Urinal (male 1-12) | [8 empty] | 0 |  | 0 | [20 empty] | 6 | 0.01 | 0.05 |  | 0.01 | 0.05 | Friday | 50
DHW Heater Outlet Temp (Restroom service) |  | 140 |  | Information from Plumbing Schedules | Conventional Water Closet (female 1-12) | [8 empty] | 0 |  | 0 | [20 empty] | 7 | 0.1 | 0.05 |  | 0.01 | 0.05 | Saturday | 52
Insert Total Number of Students Served by Kitchen |  | 0 | 0 | May be different than students in Project Area (ie. Additions) | [32 empty] | 8 | 0.3 | 0.05 |  | 0.01 | 0.05 | Sunday | 52
Dishwasher racks (if not included in the kitchen equipment tab) |  | 0 |  |  | Reference Table 2: Daily Sewage Volumes (gallons) | [20 empty] | CW + DHW |  |  | Design case | [7 empty] | 9 | 0.3 | 0.05 |  | 0.01 | 0.05 | Total (must equal 365 days/year) | 365
[14 empty] | Base Case | [5 empty] | Design Case | [5 empty] | Gal/day |  | Gal/year |  |  |  |  | DHW |  |  |  | 10 | 0.2 | 0.05 |  | 0.01 | 0.05
Model Inputs | [13 empty] | Daily Uses | Flowrate (gpm or gpc) |  | Duration (Flush) | Regular Sewage Generated | Summer Sewage Generated | Daily Uses | Flowrate (gpm or gpc) | Duration (Flush) | Regular Sewage Generated | Summer Sewage Generated | [5 empty] | Outlet T |  |  | Gal/day |  | Gal/year | Gal/min | 11 | 0.2 | 0.05 |  | 0.01 | 0.05 | WD | 250
Process Loads to DHW Loop | [25 empty] | Reg | Summer |  |  | F | DHW % | Correction factor | Reg | Summer |  |  | 12 | 0.5 | 0.4 |  | 0.01 | 0.05 | WEH | 115
|  | HW GPM input |  |  | Flow Fixtures | Conventional Lavatory (Student) (cycle) | [7 empty] | 6 | 0.25 |  | 1 | 0 | 0 | 6 | 0.04 | 1 | 0 | 0 |  | 0 | 0 |  | Conventional Lavatory (Student) (cycle) | 95 | 45.78% | 1 | 0 | 0 | 0 | 0 | 13 | 0.5 | 0.4 |  | 0.01 | 0.05
Description | Schedule | Proposed | LL32 Baseline | GSG Baseline |  | Conventional Lavatory (Adult) (cycle) | [7 empty] | 6 | 0.25 |  | 1 | 0 | 0 | 6 | 0.04 | 1 | 0 | 0 |  | 0 | 0 |  | Conventional Lavatory (Adult) (cycle) | 95 | 45.78% | 1 | 0 | 0 | 0 | 0 | 14 | 0.3 | 0.4 |  | 0.01 | 0.05
Restroom Loads | DHWSCH | 0 | 0 | 0 |  | Shower (gpm, seconds) | [7 empty] | 0.1 | 2.5 |  | 1 | 0 | 0 | 0.1 | 1.8 | 1 | 0 | 0 |  | 0 | 0 |  | Shower (gpm, seconds) | 105 | 57.83% | 1 | 0 | 0 | 0 | 0 | 15 | 0.2 | 0.05 |  | 0.01 | 0.05
Kitchen Loads | KITHW-SCH | 0 | 0 | 0 |  | Hand Sink (cycle) | [7 empty] | 4 | 0.25 |  | 1 | 0 | 0 | 4 | 0.125 | 1 | 0 | 0 |  | 0 | 0 |  | Hand Sink (cycle) | 95 | 45.78% | 1 | 0 | 0 | 0 | 0 | 16 | 0.2 | 0.05 |  | 0.01 | 0.05
[25 empty] | Total | 0 | 0 | 0 | Total |  |  |  | 0 | 0 | 0 | 0 | 17 | 0.1 | 0.05 |  | 0.01 | 0.05
[5 empty] | Flush Fixtures | Conventional Water Closet (male 1-12) | [7 empty] | 1 | 1.6 |  | 1 | 0 | 0 | 1 | 1.28 | 1 | 0 | 0 | [12 empty] | 18 | 0.1 | 0.05 |  | 0.01 | 0.05
[6 empty] | Conventional Urinal (male 1-12) | [7 empty] | 2 | 1 |  | 1 | 0 | 0 | 2 | 0.125 | 1 | 0 | 0 | [9 empty] | Toilet | 0 | 0 | 19 | 0.1 | 0.05 |  | 0.01 | 0.05
[6 empty] | Conventional Water Closet (female 1-12) | [7 empty] | 3 | 1.6 |  | 1 | 0 | 0 | 3 | 1.28 | 1 | 0 | 0 | [9 empty] | Kitchen sink | 0 | 0 | 20 | 0.1 | 0.05 |  | 0.01 | 0.05
[6 empty] | Conventional Water Closet (PK, K class rm w/ toilet) | [7 empty] | 3 | 1.6 |  | 1 | 0 | 0 | 3 | 1.28 | 1 | 0 | 0 | [9 empty] | Kitchen total |  | 0 | 21 | 0.01 | 0.05 |  | 0.01 | 0.05
[6 empty] | Conventional Water Closet (D75 class rm w/ toilet) | [7 empty] | 3 | 1.6 |  | 1 | 0 | 0 | 3 | 1.28 | 1 | 0 | 0 | [12 empty] | 22 | 0.01 | 0.05 |  | 0.01 | 0.05
[6 empty] | Conventional Water Closet (adult) | [7 empty] | 3 | 1.6 |  | 1 | 0 | 0 | 3 | 1.28 | 1 | 0 | 0 | [12 empty] | 23 | 0.01 | 0.05 |  | 0.01 | 0.05
[5 empty] | BASE CASE TOTALS | [12 empty] | 0 | 0 | DESIGN CASE TOTALS |  |  | 0 | 0 |  |  |  |  | Baseline case | [7 empty] | 24 | 0.01 | 0.05 |  | 0.01 | 0.05
[33 empty] | DHW |  |  |  | FLH/day | 3.3 | 2.25 |  | 0.24 | 1.2
[5 empty] | Regular Operation + Summer Operation Summary | [24 empty] | Outlet T |  |  | Gal/day |  | Gal/year | Gal/min
[18 empty] | Base Case |  | Design Case | [9 empty] | F | DHW % | Correction factor | Reg | Summer |  |  | FLH/year | 852.6 | 700.5
[5 empty] | Total "Regular Operation" + Summer Operation" Annual Volume | [12 empty] | 0 |  | 0 | [8 empty] | Conventional Lavatory (Student) (cycle) | 95 | 45.78% | 1 | 0 | 0 | 0 | 0
[5 empty] | Total: Water Use Reduction for "Regular Operation" + "Summer Operation" | [14 empty] | 0% | [8 empty] | Conventional Lavatory (Adult) (cycle) | 95 | 45.78% | 1 | 0 | 0 | 0 | 0
[29 empty] | Shower (gpm, seconds) | 105 | 57.83% | 1 | 0 | 0 | 0 | 0
[29 empty] | Hand Sink (cycle) | 95 | 45.78% | 1 | 0 | 0 | 0 | 0
[29 empty] | Total |  |  |  | 0 | 0 | 0 | 0
[34 empty] | Toilet | 0 | 0
[5 empty] | Table 3. Standards for appliances and processes | [28 empty] | Kitchen sink | 0 | 0
[5 empty] | Kitchen/Culinary Art Lab Equipment | Requirement |  |  | Gal/cycle | Gal/h | Gal/min | Quantity | [21 empty] | Kitchen total |  | 0
[5 empty] | Dishwasher Undercounter | ≤ 1.6 | gal/rack |  | 1.6 | 1.6 | 0.026667 | 0 | assuming 2 racks/unit
[5 empty] | Food steamer Batch | ≤ 6 | gal/hour/pan |  |  | 6 | 0.1 | 0 | typically only has cold water connections
[5 empty] | Pre-rinse spray valves | ≤ 1.3 | gpm |  |  |  | 1.3 | 0
[5 empty] | Combination Oven | ≤ 3.5 | gal/hour |  |  | 3.5 | 0.058333 | 0 | typically only has cold water connections
[5 empty] | GSG Kitchen total | 0
2019 ASHRAE HVAC applications chapter 51.15 table 6
Gal/meal
[5 empty] | Food service A - full meal restaurants and cafeterias |  |  | 2.4
[5 empty] | DHW correction factor for ASHRAE values that may be outdated | 1
[5 empty] | DHW Gal/meal | 2.4 | 2.4
[5 empty] | DHW GAL/year | 0 | 0
[5 empty] | raw HW GPM | 0 | 0
[6 empty] | Design | Baseline
[5 empty] | Adjusted meal HW GPM | 0 | 0
2019 ASHRAE HVAC applications chapter 51.21 table 10
[6 empty] | Gal/h of water at 140F |  | GPM of water at 140F
[5 empty] | Service sink | 20 |  | 0.33333
[5 empty] | Pantry sink | 10 |  | 0.16667
[5 empty] | Kitchen sink | 20 |  | 0.33333
[5 empty] | Circular wash sink | 30 |  | 0.5
[5 empty] | Semicircular wash sink | 15 |  | 0.25
2019 ASHRAE HVAC applications chapter 51.22 table 11
[7 empty] | GPM | Quantity | Assumed run/h
[5 empty] | One compartment food preparation sink |  | 2
[5 empty] | Two compartment food preparation sink |  | 2
[5 empty] | Mop sink or can wash |  | 2 | 0 | 0.1
Note on BH19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Does not include cooking and mop sinks
Note on BH34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Does not include cooking and mop sinks
Note on O53: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: assumed based on the overall building water reduction; DHW is not used for cooking food, only for washing utensils and dishes

## Kitchen Instructions
Complete the Kitchen Equipment tab per the Kitchen Equipment Schedule
Complete Orange cells for all equipment on the schedule
For electrical equipment, either the blue
or purple cells should be completed.
Notes:
If the kitchen has natural gas, the natural gas equipment section should be completed. The natural gas appliances have electric component accounted for in Rows 9-12
If the kitchen is all electric, then the electric cooking equipment in rows 79-82 should be included
Leave the amps, volts, phase, and kW blank for items whose electric loads are included in another piece of equipment, such as milk coolers, water dispensers, etc.
Leave the amps, volts, phase, and kW blank for the fire suppression system.
Ventilator hood load should be included as a direct load on the Kitchen Fan Meter.
It may be easier for accounting purposes to keep the kitchen equipment separate from the servery equipment, but it is not necessary.
Default values for each equipment type have been provided. These values should be updated to match the kitchen schedule when available.
Complete the Input to eQuest tab
Input the kitchen and servery areas as noted.
Update the space equipment and source loads as noted.
Copy schedules to eQuest

## Kitchen Equipment
| Item # | Description | Qty | kW | Amps | Volts | Phase | W each | Total kW |  | ASHRAE 2017 Reference | Rated Btu/h | Usage Factor | Resulting Power | Diversity Factor | Hours of Operation | Hours per Day | Daily (Source kBtu) | Yearly (Source kBtu) | Fraction | Energy Star | Days/yr |  | Energy model | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
|  | Total | [6 empty] | 0 |  |  |  |  | kW |  |  |  |  | 0
Kitchen |  | Sink Agitator | 0 |  | 5.6 | 120 | 1 | 672 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-3pm | 8 | 0 | 0 | #DIV/0! |  | 251 | 0 | Sink Agitator | bar: 8 to 15
|  | Pot wash sink | 0 |  | 0 | 0 | 0 | 0 | 0 | bar: 8 to 9; 12 to 15
|  | Mop sink | 0 |  | 0 | 0 | 0 | 0 | 0 | bar: 8 to 9; 12 to 15
|  | Sink Heater | 0 | 9 | 25 | 208 | 3 | 9000 | 0 |  | Booster heater | 130000 | 0.1 | 0 | 1 | 7am-3pm | 8 | 0 | 0 | #DIV/0! |  | 251 | 0 | Sink Heater | 8: 0.1; 9: 0.1; 10: 0.1; 11: 0.1; 12: 0.1; 13: 0.1; 14: 1; 15: 0.1
|  | Ventilator Hood | 0 |  | 10 | 120 | 1 | 1200 |  |  | NA | NA | 1 | 0 | 1 | 7am-1pm; School Days; This load is for the hood lights only | 6 | 0 | 0 | #DIV/0! |  | 251 | 0 | Ventilator Hood | bar: 10 to 15
|  | Hood Fire Suppression System | Not typically on | 0 | [18 empty] | 0 | Hood Fire Suppression System
|  | Gas Tilt Skillet |  |  | 1.8 | 120 | 1 | 216 | 0 |  | NA | NA | 1 | 0 | 0.3 | Assume 2 hours, Used on Demand; School Days | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Gas Tilt Skillet | bar: 10 to 11
|  | Gas fired Steamer |  | 0.1 |  | 120 | 1 | 100 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-1pm; School Days | 6 | 0 | 0 | #DIV/0! |  | 251 | 0 | Gas fired Steamer | bar: 8 to 13
|  | Natural Gas Dbl. Deck Convection Oven |  |  | 6 | 120 | 1 | 720 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-1pm; School Days | 6 | 0 | 0 | #DIV/0! |  | 251 | 0 | Natural Gas Dbl. Deck Convection Oven | bar: 8 to 13
|  | Natural Gas 4-Burner Range w/ Oven |  |  | 15 | 120 | 1 | 1800 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-1pm; School Days | 6 | 0 | 0 | #DIV/0! |  | 251 | 0 | Natural Gas 4-Burner Range w/ Oven | bar: 8 to 13
|  | Reach-In Freezer 1 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 1 | bar: 1 to 24
|  | Reach-In Freezer 2 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 2 | bar: 1 to 24
|  | Reach-In Freezer 3 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 3 | bar: 1 to 24
|  | Reach-In Freezer 4 |  |  | 9.4 | 120 | 1 | 1128 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 4 | bar: 1 to 24
|  | Reach-in Refrigerator 1 |  |  | 7 | 120 | 1 | 840 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 1 | bar: 1 to 24
|  | Reach-in Refrigerator 2 |  |  | 7 | 120 | 1 | 840 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 2 | bar: 1 to 24
|  | Reach-in Refrigerator 3 |  |  | 7 | 120 | 1 | 840 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 3 | bar: 1 to 24
|  | Reach-in Refrigerator 4 |  |  | 7 | 120 | 1 | 840 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 4 | bar: 1 to 24
|  | Mobile Heated Cabinet 1 |  | 1.5 | 12 | 120 | 1 | 1500 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 1 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Mobile Heated Cabinet 2 |  | 1.5 | 12 | 120 | 1 | 1500 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 2 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Mobile Heated Cabinet 3 |  | 1.5 | 12 | 120 | 1 | 1500 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 3 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Mobile Heated Cabinet 4 |  | 1.5 | 12 | 120 | 1 | 1500 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 4 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Cook's Table w/ Sink | 0 |  | 7 | 120 | 1 | 840 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days; These are convenience outlets for the staff to use for any owner supplied equipment such as blenders, mixers that would be used on demand for a short time. Assume 7.0 amps | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Cook's Table w/ Sink | bar: 10 to 11
|  | Work Table 1 | 0 |  | 7 | 120 | 1 | 840 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days; These are convenience outlets for the staff to use for any owner supplied equipment such as blenders, mixers that would be used on demand for a short time. Assume 7.0 amps | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Work Table 1 | bar: 10 to 11
|  | Work Table 2 |  |  | 7 | 120 | 1 | 840 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days; These are convenience outlets for the staff to use for any owner supplied equipment such as blenders, mixers that would be used on demand for a short time. Assume 7.0 amps | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Work Table 2 | bar: 10 to 11
|  | Work Table 3 |  |  | 7 | 120 | 1 | 840 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days; These are convenience outlets for the staff to use for any owner supplied equipment such as blenders, mixers that would be used on demand for a short time. Assume 7.0 amps | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Work Table 3 | bar: 10 to 11
|  | Work Table 4 |  |  | 7 | 120 | 1 | 840 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days; These are convenience outlets for the staff to use for any owner supplied equipment such as blenders, mixers that would be used on demand for a short time. Assume 7.0 amps | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Work Table 4 | bar: 10 to 11
|  | Can Opener |  |  | 1.2 | 120 | 1 | 144 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Can Opener | bar: 10 to 11
|  | Food Processor |  |  | 6 | 120 | 1 | 720 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Food Processor | bar: 10 to 11
|  | Slicer |  |  | 6 | 120 | 1 | 720 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Slicer | bar: 10 to 11
Can Wash |  | Power Wash Station |  |  | 12 | 120 | 1 | 1440 | 0 |  | Dishwasher, door type, chemical sanitizing, dump and fill | 6100 | 0.49 | 0 | 1 |  | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Power Wash Station | 14: 0.0049
Hall/Office |  | Time Card Recorder W/ Card Racks | 0 |  | 10 | 120 | 1 | 1200 | 0 |  | NA | NA | 1 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! |  | 365 | 1 | Time Card Recorder W/ Card Racks | bar: 1 to 24
Servery |  | Mobile Heated Cabinet 1 |  | 1.5 | 12 | 120 | 1 | 1500 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 1 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Mobile Heated Cabinet 2 |  | 1.5 | 12 | 120 | 1 | 1500 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 2 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Mobile Heated Cabinet 3 |  | 1.5 | 12 | 120 | 1 | 1500 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 3 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Mobile Heated Cabinet 4 |  | 1.5 | 12 | 120 | 1 | 1500 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 4 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Reach-in Refrigerator 1 |  |  | 8.2 | 120 | 1 | 984 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 1 | bar: 1 to 24
|  | Reach-in Refrigerator 2 |  |  | 8.2 | 120 | 1 | 984 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 2 | bar: 1 to 24
|  | Reach-in Refrigerator 3 |  |  | 8.2 | 120 | 1 | 984 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 3 | bar: 1 to 24
|  | Reach-in Refrigerator 4 |  |  | 8.2 | 120 | 1 | 984 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 4 | bar: 1 to 24
|  | Reach-In Freezer 1 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 1 | bar: 1 to 24
|  | Reach-In Freezer 2 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 2 | bar: 1 to 24
|  | Reach-In Freezer 3 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 3 | bar: 1 to 24
|  | Reach-In Freezer 4 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 4 | bar: 1 to 24
|  | Mobile Hot Food Counter 1 |  |  | 40.2 | 208 | 1 | 8361.6 | 0 |  | Cabinet: proofing (large) | 17400 | 0.08 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Hot Food Counter 1 | 9: 0.04; 10: 0.08; 11: 0.08; 12: 0.5; 13: 1; 14: 1
|  | Mobile Hot Food Counter 2 |  |  | 40.2 | 208 | 1 | 8361.6 | 0 |  | Cabinet: proofing (large) | 17400 | 0.08 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Hot Food Counter 2 | 9: 0.04; 10: 0.08; 11: 0.08; 12: 0.5; 13: 1; 14: 1
|  | Mobile Hot Food Counter 3 |  |  | 40.2 | 208 | 1 | 8361.6 | 0 |  | Cabinet: proofing (large) | 17400 | 0.08 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Hot Food Counter 3 | 9: 0.04; 10: 0.08; 11: 0.08; 12: 0.5; 13: 1; 14: 1
|  | Mobile Salad Counter |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | Mobile Salad Counter
|  | Water Dispenser |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | Water Dispenser
|  | Milk Cooler |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | Milk Cooler
|  | Mobile Cashier Counter 1 |  |  | 10 | 120 | 1 | 1200 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Cashier Counter 1 | bar: 9 to 13
|  | Mobile Cashier Counter 2 |  |  | 10 | 120 | 1 | 1200 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Cashier Counter 2 | bar: 9 to 13
|  | Mobile Cashier Counter 3 |  |  | 10 | 120 | 1 | 1200 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Cashier Counter 3 | bar: 9 to 13
|  | Mobile Cashier Counter 4 |  |  | 10 | 120 | 1 | 1200 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Cashier Counter 4 | bar: 9 to 13
|  | P.O.S. Unit 1 |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | P.O.S. Unit 1
|  | P.O.S. Unit 2 |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | P.O.S. Unit 2
|  | P.O.S. Unit 3 |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | P.O.S. Unit 3
|  | P.O.S. Unit 4 |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | P.O.S. Unit 4
[9 empty] | 0 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
[17 empty] | #REF! | [5 empty] | Average, weekday |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[23 empty] | Average, WEH |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Electric | [5 empty] | Gas | Usage Factors
| Item # | Description | Qty | Rated Power | Amperage | Voltage | Phase | Calculated Power | Calculated Power | Gas Power (each unit) | ASHRAE 2017 Usage Factor Reference | Usage Factor | Resulting Power | Diversity Factor | Hours of Operation | Hours per Day | Daily | Days | Yearly |  | Percent of Base |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Gas Fired Kitchen |  | TILT SKILLET | [7 empty] | 130000 | Tilting Skillet/braising pan (gas) | 0.1 | 3.8101 | 1 | Assume 2 hours, Used on Demand; School Days | 2 | 0 | 251 | 0 |  |  |  |  | TILT SKILLET | bar: 10 to 11
|  | STEAMER | 0 | [6 empty] | 200000 | Steam kettle, large (gas) | 0.04 | 2.3447 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  |  | STEAMER | bar: 8 to 13
|  | DBL. DECK. CONVECTION OVEN x2 | 0 | [6 empty] | 110000 | Oven, combi (gas) | 0.08 | 2.5791 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  |  | DBL. DECK. CONVECTION OVEN x2 | bar: 8 to 13
|  | COMBI RANGE W/ OVEN | 0 | [6 empty] | 180000 | Range top, 6 elements on/oven on (gas) | 0.85 | 44.8417 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  |  | COMBI RANGE W/ OVEN | bar: 8 to 13
|  | Total | [7 empty] | 0 |  | #DIV/0! | [5 empty] | Total | 0 |  | #REF! |  |  | Total | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
All Electric Kitchen |  | TILT SKILLET |  | 18 | 50 | 208 | 3 | 18013.3284 | 18.0133 |  | Tilting Skillet/braising pan (electric) | 0.16 | 2.88 | 1 | Assume 2 hours, Used on Demand; School Days | 2 | 0 | 251 | 0 |  |  |  |  | TILT SKILLET | bar: 10 to 11
|  | CONVECTION STEAMER |  | 10.7 | 29.8 | 208 | 3 | 10735.9437 | 10.7359 |  | Steam kettle, large (electric) | 0.04 | 0.428 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  |  | CONVECTION STEAMER | bar: 8 to 13
|  | COMBI OVEN |  | 16.5 | 45.7 | 208 | 3 | 16464.1822 | 16.4642 |  | Oven, combi (electric) | 0.1 | 1.65 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  |  | COMBI OVEN | bar: 8 to 13
|  | INDUCTION RANGE |  | 21.1 | 66.4 | 208 | 3 | 23921.7001 | 23.9217 |  | Range top, 6 elements on/oven on (electric) | 0.54 | 11.394 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  |  | INDUCTION RANGE | bar: 8 to 13
|  | Total | [6 empty] | 0 | [8 empty] | Total | 0 |  | #REF! |  |  | Total | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Electric
| Item # | Description | Qty | Rated Power | Amperage | Voltage | Phase | Calculated Power | Calculated Power | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Walk-in refrigerator and freezer |  | Refrigeration Rack System | 1 |  | 40.6 | 208 | 3 | 14626.8227 | 14.6268 | [13 empty] | 0 | Refrigeration Rack System | 0.061813 | 0.05151 | 0.048265 | 0.048426 | 0.057754 | 0.069322 | 0.060093 | 0.058131 | 0.059309 | 0.059794 | 0.067368 | 0.076445 | 0.072822 | 0.067629 | 0.06545 | 0.062261 | 0.062367 | 0.076948 | 0.068549 | 0.06017 | 0.056471 | 0.056012 | 0.064158 | 0.072587
|  | Walk-In Freezer (-10F) | 1 |  | 10 | 120 | 1 | 1200 | 1.2 | [13 empty] | 0 | Walk-In Freezer (-10F) | 0.017701 | 0 | 0 | 0.012391 | 0.012391 | 0.0061954 | 0.069862 | 0.075172 | 0.069862 | 0.063667 | 0.063667 | 0.063667 | 0.18138 | 0.057471 | 0.069862 | 0.012391 | 0.012391 | 0.0061954 | 0.023897 | 0 | 0.0061954 | 0.023897 | 0.0061954 | 0.0061954
|  | Freezer Blower Coil | 1 |  | 19.2 | 208 | 1 | 3993.6 | 3.9936 | [13 empty] | 0 | Freezer Blower Coil | 0.34416 | 0.38752 | 0.47335 | 0.36242 | 0.33149 | 0.33083 | 0.40743 | 0.51878 | 0.40515 | 0.39107 | 0.39875 | 0.39652 | 0.44017 | 0.5021 | 0.40948 | 0.36445 | 0.36623 | 0.35973 | 0.41751 | 0.44769 | 0.34984 | 0.34537 | 0.3447 | 0.33288
|  | Flip-Flop Controller | 1 |  | 15 | 120 | 1 | 1800 | 1.8 | [13 empty] | 1 | Flip-Flop Controller | bar: 1 to 24
|  | Walk-In Refrigerator (+35F) | 1 |  | 10 | 120 | 1 | 1200 | 1.2 | [13 empty] | 0 | Walk-In Refrigerator (+35F) | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Refrigerator Blower Coil | 1 |  | 3.2 | 120 | 1 | 384 | 0.384 | [13 empty] | 0 | Refrigerator Blower Coil | 0.1372 | 0.13582 | 0.13651 | 0.13555 | 0.13353 | 0.13669 | 0.14144 | 0.13997 | 0.14044 | 0.14192 | 0.14189 | 0.14078 | 0.13492 | 0.13795 | 0.1444 | 0.13855 | 0.13755 | 0.13851 | 0.13801 | 0.1386 | 0.13853 | 0.13705 | 0.13597 | 0.13482
|  | Flip-Flop Controller | 1 |  | 15 | 120 | 1 | 1800 | 1.8 | [13 empty] | 1 | Flip-Flop Controller | bar: 1 to 24
|  | Total | [6 empty] | 25.0044 | [13 empty] | Average, weekday | Total | 0.24 | 0.24 | 0.25 | 0.23 | 0.23 | 0.24 | 0.27 | 0.29 | 0.27 | 0.27 | 0.28 | 0.28 | 0.29 | 0.29 | 0.28 | 0.24 | 0.24 | 0.25 | 0.25 | 0.25 | 0.24 | 0.24 | 0.24 | 0.24
[23 empty] | Average, WEH |  | 0.24 | 0.24 | 0.25 | 0.24 | 0.23 | 0.24 | 0.24 | 0.25 | 0.23 | 0.23 | 0.23 | 0.24 | 0.24 | 0.25 | 0.24 | 0.23 | 0.24 | 0.24 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.23
W
|  | Walk-in lighting - WD | 1 | [5 empty] | 1.2 | [12 empty] | 120 | 0 | Walk-in lighting - WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Walk-in lighting - WEH | 1 | [5 empty] | 1.2 | [8 empty] | TILT SKILLET | 1 |  |  | 120 | 1 | Walk-in lighting - WEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | STEAMER | 1 |  |  | 924 | 0 | Freezer heater - WD | 0.02 | 0 | 0 | 0.014 | 0.014 | 0.007 | 0.014 | 0.02 | 0.014 | 0.007 | 0.007 | 0.007 | 0.14 | 0 | 0.014 | 0.014 | 0.014 | 0.007 | 0.027 | 0 | 0.007 | 0.027 | 0.007 | 0.007
[18 empty] | DBL. DECK. CONVECTION OVEN | 1 |  |  | 924 | 0 | Freezer heater - WEH | 0.02 | 0 | 0 | 0.014 | 0.014 | 0.007 | 0.014 | 0.02 | 0.014 | 0.007 | 0.007 | 0.007 | 0.14 | 0 | 0.014 | 0.014 | 0.014 | 0.007 | 0.027 | 0 | 0.007 | 0.027 | 0.007 | 0.007
|  | Freezer schedule - WD | 1 | [5 empty] | 1.2 | [8 empty] | INDUCTION RANGE W/ OVEN | 1 |  |  |  | 0 | Freezer schedule - WD | 0.017701 | 0 | 0 | 0.012391 | 0.012391 | 0.0061954 | 0.069862 | 0.075172 | 0.069862 | 0.063667 | 0.063667 | 0.063667 | 0.18138 | 0.057471 | 0.069862 | 0.012391 | 0.012391 | 0.0061954 | 0.023897 | 0 | 0.0061954 | 0.023897 | 0.0061954 | 0.0061954
|  | Freezer schedule - WEH | 1 | [5 empty] | 1.2 | [13 empty] | 1 | Freezer schedule - WEH | 0.017701 | 0 | 0 | 0.012391 | 0.012391 | 0.0061954 | 0.012391 | 0.017701 | 0.012391 | 0.0061954 | 0.0061954 | 0.0061954 | 0.12391 | 0 | 0.012391 | 0.012391 | 0.012391 | 0.0061954 | 0.023897 | 0 | 0.0061954 | 0.023897 | 0.0061954 | 0.0061954
|  | Freezer Blower schedule - WEH | 1 | [5 empty] | 3.9936 | [8 empty] | Site | Usage Factors |  |  |  | 1 | Freezer Blower schedule - WEH | 0.33774 | 0.39014 | 0.47484 | 0.39239 | 0.31104 | 0.3206 | 0.38794 | 0.45703 | 0.34313 | 0.33983 | 0.3435 | 0.37872 | 0.36128 | 0.45051 | 0.36253 | 0.34294 | 0.37565 | 0.34238 | 0.39535 | 0.44005 | 0.33956 | 0.34773 | 0.35315 | 0.33906
|  | Fridge Blower schedule - WEH | 1 | [5 empty] | 0.384 | [8 empty] | Electric | 0 |  |  |  | 1 | Fridge Blower schedule - WEH | 0.13829 | 0.13936 | 0.13424 | 0.13653 | 0.13658 | 0.1337 | 0.13842 | 0.1371 | 0.13647 | 0.13579 | 0.1387 | 0.13586 | 0.13581 | 0.1387 | 0.13763 | 0.1363 | 0.13675 | 0.13845 | 0.13691 | 0.13675 | 0.13856 | 0.13911 | 0.13568 | 0.13702
|  | Refrigeration Rack System | 1 | [5 empty] | 14.6268 | [8 empty] | Gas | 0 |  |  |  | 1 | Refrigeration Rack System -WEH | 0.064052 | 0.056721 | 0.050819 | 0.0506 | 0.054574 | 0.067761 | 0.054909 | 0.04835 | 0.046394 | 0.04968 | 0.054931 | 0.062389 | 0.059945 | 0.055059 | 0.05216 | 0.051612 | 0.054627 | 0.063577 | 0.057007 | 0.048558 | 0.04556 | 0.048138 | 0.053739 | 0.056476
[18 empty] | Difference | 0
[18 empty] | Source | Usage Factors
[18 empty] | Electric | 0
[18 empty] | Gas | 0
[18 empty] | Difference | #DIV/0!
#REF!
Conversion
[11 empty] | kW to kBtu | 3.412
Site to Source Factor
[11 empty] | Electric | 2.55
[11 empty] | Gas | 1.05
[11 empty] | Equivalent Days from Previous model | 283.6
[11 empty] | Regular + Summer Days | 251
[11 empty] | Typical Diversity | 1
[11 empty] | Lower Diversity | 0.3
Usage Factors from ASHRAE 2017
[11 empty] | Typical Usage Factor | 1
[11 empty] | Booster heater | 0.1
[11 empty] | Freezer (small) | 0.41
[11 empty] | Reach-in refrigerator | 0.25
[11 empty] | Cabinet: hot serving (large) insulated | 0.18
[11 empty] | Dishwasher, door type, chemical sanitizing, dump and fill | 0.49
[11 empty] | Cabinet: proofing (large) | 0.08
Note on E1: Values in this column will override Amp/Volt calculations for equipment power
Note on C7: Ventilator hood info should be input as a direct load to the Kitchen Fan Electric meter
Note on E8: Keep as zero. Not for typical operation
Note on C50: Typically part of hot food counter
Note on C51: Typically part of hot food counter
Note on C52: Typically part of hot food counter
Note on C57: Typically part of Mobile Cashier Counter
Note on C58: Typically part of Mobile Cashier Counter
Note on C59: Typically part of Mobile Cashier Counter
Note on C60: Typically part of Mobile Cashier Counter

## Input to eQuest
KITCHEN-EQP-WD = ( | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
KITCHEN-EQP-WEH = ( | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
KIT-SRC-GAS-WD = ( | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
KIT-SRC-ELEC-WD = ( | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Walk-in refrigeration (direct meter load) | 25.0044 | kW
Total Kitchen/ Servery Electric Equipment Load | 0 | kW
Kitchen Area | 0 | ft2 | Provide Area
Servery Area | 0 | ft2 | Provide Area
Total Area | 0 | ft2
Kitchen/ Servery Electric Equipment Load per area | 0 | W/ft2 | Input to eQuest as Input Power Density (EQUIPMENT-W/AREA)
Total Kitchen/ Servery Gas Source Load (BTU) | 0 | BTU
Kitchen Gas Source Load (BTU) | 0 |  | Input to eQuest as Input Power (Btu/h) (SOURCE-POWER)
Servery Gas Source Load (BTU) | 0 |  | Input to eQuest as Input Power (Btu/h) (SOURCE-POWER)
Total Kitchen/ Servery Electric Source Load (kW) | 0 | kW
Total Kitchen/ Servery Electric Source Load (BTU) | 0 | BTU
Total Kitchen Electric Source Load (BTU) | 0 |  | Input to eQuest as Input Power (Btu/h) (SOURCE-POWER)
Total Servery Electric Source Load (BTU) | 0 |  | Input to eQuest as Input Power (Btu/h) (SOURCE-POWER)
|  | Hour | KIT-EQP-WD = DAY-SCHEDULE | KIT-EQP-LO-D = DAY-SCHEDULE | KIT-SRC-GAS-WD = DAY-SCHEDULE | KIT-SRC-ELEC-WD = DAY SCHEDULE | KIT-WALKIN-WD = DAY-SCHEDULE | KIT-WALKIN-WEH = DAY SCHEDULE
|  |  | TYPE = FRACTION | TYPE = FRACTION | TYPE = FRACTION | TYPE = FRACTION | TYPE = FRACTION | TYPE = FRACTION
|  |  | (1,24)( | (1,24)( | (1,24)( | (1,24)( | (1,24)( | (1,24)(
|  | 1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.24
|  | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.24
|  | 3 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.25 | 0.25
|  | 4 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.23 | 0.24
|  | 5 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.23 | 0.23
|  | 6 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.24
|  | 7 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.27 | 0.24
|  | 8 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.29 | 0.25
|  | 9 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.27 | 0.23
|  | 10 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.27 | 0.23
|  | 11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.28 | 0.23
|  | 12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.28 | 0.24
|  | 13 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.29 | 0.24
|  | 14 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.29 | 0.25
|  | 15 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.28 | 0.24
|  | 16 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.23
|  | 17 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.24
|  | 18 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.25 | 0.24
|  | 19 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.25 | 0.24
|  | 20 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.25 | 0.24
|  | 21 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.23
|  | 22 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.23
|  | 23 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.23
|  | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.24 | 0.24
|  |  | ) | ) | ) | ) | ) | )
|  |  | .. | .. | .. | .. | .. | ..

## Default values (hidden)
| Item # | Description | Qty | kW | Amps | Volts | Phase | W each | Total kW |  | ASHRAE 2017 Reference | Rated Btu/h | Usage Factor | Resulting Power | Diversity Factor | Hours of Operation | Hours per Day | Daily (Source kBtu) | Yearly (Source kBtu) | Fraction | Energy Star | Days/yr |  | Energy model | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
|  | Total | [6 empty] | 0 |  |  |  |  | kW |  |  |  |  | 0
Kitchen |  | Sink Agitator |  |  | 5.6 | 120 | 1 | 672 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-3pm | 8 | 0 | 0 | #DIV/0! |  | 251 | 0 | Sink Agitator | bar: 8 to 15
|  | Sink Heater |  | 9 | 25 | 208 | 3 | 9000 | 0 |  | Booster heater | 130000 | 0.1 | 0 | 1 | 7am-3pm | 8 | 0 | 0 | #DIV/0! |  | 251 | 0 | Sink Heater | 8: 0.1; 9: 0.1; 10: 0.1; 11: 0.1; 12: 0.1; 13: 0.1; 14: 1; 15: 0.1
|  | Ventilator Hood |  |  | 10 | 120 | 1 | 1200 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-1pm; School Days; This load is for the hood lights only | 6 | 0 | 0 | #DIV/0! |  | 251 | 0 | Ventilator Hood | bar: 10 to 15
|  | Hood Fire Suppression System | Not typically on | 0 | [18 empty] | 0 | Hood Fire Suppression System
|  | Gas Tilt Skillet |  |  | 1.8 | 120 | 1 | 216 | 0 |  | NA | NA | 1 | 0 | 0.3 | Assume 2 hours, Used on Demand; School Days | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Gas Tilt Skillet | bar: 10 to 11
|  | Gas fired Steamer |  | 0.1 |  | 120 | 1 | 100 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-1pm; School Days | 6 | 0 | 0 | #DIV/0! |  | 251 | 0 | Gas fired Steamer | bar: 8 to 13
|  | Natural Gas Dbl. Deck Convection Oven |  |  | 6 | 120 | 1 | 720 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-1pm; School Days | 6 | 0 | 0 | #DIV/0! |  | 251 | 0 | Natural Gas Dbl. Deck Convection Oven | bar: 8 to 13
|  | Natural Gas 4-Burner Range w/ Oven |  |  | 15 | 120 | 1 | 1800 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-1pm; School Days | 6 | 0 | 0 | #DIV/0! |  | 251 | 0 | Natural Gas 4-Burner Range w/ Oven | bar: 8 to 13
|  | Reach-In Freezer 1 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 1 | bar: 1 to 24
|  | Reach-in Refrigerator 1 |  |  | 7 | 120 | 1 | 840 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 1 | bar: 1 to 24
|  | Mobile Heated Cabinet 1 |  | 1.5 | 12 | 120 | 1 | 1440 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 1 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Cook's Table w/ Sink |  |  | 7 | 120 | 1 | 840 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days; These are convenience outlets for the staff to use for any owner supplied equipment such as blenders, mixers that would be used on demand for a short time. Assume 7.0 amps | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Cook's Table w/ Sink | bar: 10 to 11
|  | Work Table 1 |  |  | 7 | 120 | 1 | 840 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days; These are convenience outlets for the staff to use for any owner supplied equipment such as blenders, mixers that would be used on demand for a short time. Assume 7.0 amps | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Work Table 1 | 10: #REF!; 11: #REF!
|  | Can Opener |  |  | 1.2 | 120 | 1 | 144 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Can Opener | bar: 10 to 11
|  | Food Processor |  |  | 6 | 120 | 1 | 720 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Food Processor | bar: 10 to 11
|  | Slicer |  |  | 6 | 120 | 1 | 720 | 0 |  | NA | NA | 1 | 0 | 1 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Slicer | bar: 10 to 11
Ref/Freeze |  | Walk-In Freezer (-10F) |  |  | 10 | 120 | 1 | 1200 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! |  | 365 | 1 | Walk-In Freezer (-10F) | 0.41 | 0.41 | 0.41 | 1 | 0.41 | 0.41 | 0.41 | 1 | 0.41 | 0.41 | 0.41 | 1 | 0.41 | 0.41 | 0.41 | 1 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41 | 0.41
|  | Blower Coil |  |  | 11.9 | 208 | 1 | 2475.2 | 0 |  | NA | NA | 1 | 0 | 1 | Unit will consume 11.9 amps for the defrost cycle which runs for a total of 90 minutes per day; otherwise will consume 1.8 amps for the rest of the day. | 1.5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Blower Coil | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 1 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | Flip-Flop Controller |  |  | 15 | 120 | 1 | 1800 | 0 |  | NA | NA | 1 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! |  | 251 | 0 | Flip-Flop Controller | bar: 1 to 24
|  | Walk-In Refrigerator (+35F) |  |  | 10 | 120 | 1 | 1200 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! |  | 365 | 1 | Walk-In Refrigerator (+35F) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  | Blower Coil |  |  | 1.8 | 120 | 1 | 216 | 0 |  | NA | NA | 1 | 0 | 1 | 24/7 | 22.5 | 0 | 0 | #DIV/0! |  | 365 | 1 | Blower Coil |  | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Flip-Flop Controller |  |  | 15 | 120 | 1 | 1800 | 0 |  | NA | NA | 1 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! |  | 365 | 1 | Flip-Flop Controller | bar: 1 to 24
Roof |  | Refrigeration Rack System* |  |  | 0 | 208 | 3 | 0 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7; Located on Roof | 24 | 0 | 0 | #DIV/0! |  | 365 | 1 | Refrigeration Rack System* | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Can Wash |  | Power Wash Station |  |  | 12 | 120 | 1 | 1440 | 0 |  | Dishwasher, door type, chemical sanitizing, dump and fill | 6100 | 0.49 | 0 | 1 |  | 2 | 0 | 0 | #DIV/0! |  | 251 | 0 | Power Wash Station | 14: 0.0049
Hall/Office |  | Time Card Recorder W/ Card Racks |  |  | 10 | 120 | 1 | 1200 | 0 |  | NA | NA | 1 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! |  | 365 | 1 | Time Card Recorder W/ Card Racks | bar: 1 to 24
Servery |  | Mobile Heated Cabinet 1 |  | 1.5 | 12 | 120 | 1 | 1440 | 0 |  | Cabinet: hot serving (large) insulated | 6800 | 0.18 | 0 | 0.3 | 7am-2pm; School Days | 7 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Heated Cabinet 1 | 8: 0.09; 9: 0.18; 10: 0.18; 11: 0.18; 12: 0.5; 13: 1; 14: 1; 15: 1
|  | Reach-in Refrigerator 1 |  |  | 8.2 | 120 | 1 | 984 | 0 |  | Reach-in refrigerator | 4800 | 0.25 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 1014.7 | 365 | 1 | Reach-in Refrigerator 1 | bar: 1 to 24
|  | Reach-In Freezer 1 |  |  | 15.7 | 120 | 1 | 1884 | 0 |  | Freezer (small) | 2700 | 0.41 | 0 | 1 | 24/7 | 24 | 0 | 0 | #DIV/0! | 3609.85 | 365 | 1 | Reach-In Freezer 1 | bar: 1 to 24
|  | Mobile Hot Food Counter 1 |  |  | 40.2 | 208 | 1 | 8361.6 | 0 |  | Cabinet: proofing (large) | 17400 | 0.08 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Hot Food Counter 1 | 9: 0.04; 10: 0.08; 11: 0.08; 12: 0.5; 13: 1; 14: 1
|  | Mobile Salad Counter |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | Mobile Salad Counter
|  | Mobile Cashier Counter 1 |  |  | 10 | 120 | 1 | 1200 | 0 |  | NA | NA | 1 | 0 | 0.3 | 7am-8am; 10am-2pm; School Days | 5 | 0 | 0 | #DIV/0! |  | 251 | 0 | Mobile Cashier Counter 1 | 9: #REF!; 10: #REF!; 11: #REF!; 12: #REF!; 13: #REF!
|  | P.O.S. Unit 1 |  | 0 |  |  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0 | P.O.S. Unit 1
*Accounted for separately in model as HVAC conditioning load, not as separate piece of equipment. | [8 empty] | 0 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
[17 empty] | #REF! | [5 empty] | Average, weekday | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[23 empty] | Average, WEH | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Electric | [5 empty] | Gas | Usage Factors
| Item # | Description | Qty | Rated Power | Amperage | Voltage | Phase | Calculated Power | Calculated Power | Gas Power (each unit) | ASHRAE 2017 Usage Factor Reference | Usage Factor | Resulting Power | Diversity Factor | Hours of Operation | Hours per Day | Daily | Days | Yearly |  | Percent of Base
Gas Fired Kitchen |  | TILT SKILLET | [7 empty] | 130000 | Tilting Skillet/braising pan (gas) | 0.1 | 3.8101 | 1 | Assume 2 hours, Used on Demand; School Days | 2 | 0 | 251 | 0 |  |  |  | TILT SKILLET | bar: 9 to 10
|  | STEAMER | [7 empty] | 200000 | Steam kettle, large (gas) | 0.04 | 2.3447 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  | STEAMER | bar: 7 to 12
|  | DBL. DECK. CONVECTION OVEN x2 | [7 empty] | 110000 | Oven, combi (gas) | 0.08 | 2.5791 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  | DBL. DECK. CONVECTION OVEN x2 | bar: 7 to 12
|  | COMBI RANGE W/ OVEN | [7 empty] | 180000 | Range top, 6 elements on/oven on (gas) | 0.85 | 44.8417 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  | COMBI RANGE W/ OVEN | bar: 7 to 12
|  | Total | [7 empty] | 0 |  | #DIV/0! | [5 empty] | Total | 0 |  | #REF! |  | Total | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
All Electric Kitchen |  | TILT SKILLET |  | 18 | 50 | 208 | 3 | 18013.3284 | 18.0133 |  | Tilting Skillet/braising pan (electric) | 0.16 | 2.88 | 1 | Assume 2 hours, Used on Demand; School Days | 2 | 0 | 251 | 0 |  |  |  | TILT SKILLET | bar: 9 to 10
|  | STEAMER |  | 32.2 | 89.5 | 208 | 3 | 32243.8578 | 32.2439 |  | Steam kettle, large (electric) | 0.04 | 1.288 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  | STEAMER | bar: 7 to 12
|  | DBL. DECK. CONVECTION OVEN |  | 11 | 31 | 208 | 3 | 11168.2636 | 11.1683 |  | Oven, combi (electric) | 0.1 | 1.1 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  | DBL. DECK. CONVECTION OVEN | bar: 7 to 12
|  | INDUCTION RANGE W/ OVEN |  | 26.8 | 82.2 | 208 | 3 | 29613.9119 | 29.6139 |  | Range top, 6 elements on/oven on (electric) | 0.54 | 14.472 | 1 | 7am-1pm; School Days | 6 | 0 | 251 | 0 |  |  |  | INDUCTION RANGE W/ OVEN | bar: 7 to 12
|  | Total | [6 empty] | 0 | [8 empty] | Total | 0 |  | #REF! |  | Total | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[18 empty] | TILT SKILLET | 1
[18 empty] | STEAMER | 1
[18 empty] | DBL. DECK. CONVECTION OVEN | 1
[18 empty] | INDUCTION RANGE W/ OVEN | 1
[18 empty] | Site | Usage Factors
[18 empty] | Electric | 0
[18 empty] | Gas | 0
[18 empty] | Difference | 0
[18 empty] | Source | Usage Factors
[18 empty] | Electric | 0
[18 empty] | Gas | 0
[18 empty] | Difference | #DIV/0!
#REF!
Conversion
[11 empty] | kW to kBtu | 3.412
Site to Source Factor
[11 empty] | Electric | 2.8
[11 empty] | Gas | 1.05
[11 empty] | Equivalent Days from Previous model | 283.6
[11 empty] | Regular + Summer Days | 251
[11 empty] | Typical Diversity | 1
[11 empty] | Lower Diversity | 0.3
Usage Factors from ASHRAE 2017
[11 empty] | Typical Usage Factor | 1
[11 empty] | Booster heater | 0.1
[11 empty] | Freezer (small) | 0.41
[11 empty] | Reach-in refrigerator | 0.25
[11 empty] | Cabinet: hot serving (large) insulated | 0.18
[11 empty] | Dishwasher, door type, chemical sanitizing, dump and fill | 0.49
[11 empty] | Cabinet: proofing (large) | 0.08
Note on E6: Keep as zero. Not for typical operation
Note on F25: Use 0- not a kitchen load
Note on C32: Typically part of hot food counter
Note on C34: Typically part of Mobile Cashier Counter

## Pool inputs
[11 empty] | ASHRAE method | Dectron method
[9 empty] | Hour | Active / Inactive | POOL-VAP-SCH = DAY-SCHEDULE | POOL-VAP-SCH = DAY-SCHEDULE
Common inputs | [10 empty] | TYPE = FRACTION | TYPE = FRACTION
Pool water temp. | 82 | F | [8 empty] | (1,24)( | (1,24)(
Air temp. | 82 | F | [6 empty] | 1 | Inactive | 0.80639 | 0.83333
Pool width | 14 | ft | [6 empty] | 2 | Inactive | 0.80639 | 0.83333
Pool length | 82 | ft | [6 empty] | 3 | Inactive | 0.80639 | 0.83333
Ap: Pool area | 1148 | ft^2 | [6 empty] | 4 | Inactive | 0.80639 | 0.83333
hfg: Enthalpy of vaporization | 1048.03 | Btu/lbm | [6 empty] | 5 | Inactive | 0.80639 | 0.83333
Active hours | 15 | [7 empty] | 6 | Inactive | 0.80639 | 0.83333
density of water | 8.33 | lbm/gal | [6 empty] | 7 | Active | 1 | 1
cold water temperature | 55 | F | [6 empty] | 8 | Active | 1 | 1
Heater supply T | 140 | F | [6 empty] | 9 | Active | 1 | 1
Cold water % of total supply | 68.24% | [7 empty] | 10 | Active | 1 | 1
Hot water % of total supply | 31.76% | [7 empty] | 11 | Active | 1 | 1
[9 empty] | 12 | Active | 1 | 1
[9 empty] | 13 | Active | 1 | 1
See 2019 ASHRAE HVAC Applications chapter 6, page 6.5 |  |  |  | Calculations using Dectron pool design guide |  |  |  |  | 14 | Active | 1 | 1
[9 empty] | 15 | Active | 1 | 1
Pool water evaporation |  |  |  | Pool water evaporation |  |  |  |  | 16 | Active | 1 | 1
pw | 1.033 | in Hg |  | AF: Activity factor | 0.8 |  |  |  | 17 | Active | 1 | 1
pa (active hours) | 0.66059 | in Hg |  | ERF60: Evaporation rate factor, active hours | 0.036 | lbm/h*ft^2 | ERF60 |  | 18 | Active | 1 | 1
pa (inactive hours) | 0.55251 |  |  | ER: Evaporation rate, active hours | 33.0624 | lbm/h |  |  | 19 | Active | 1 | 1
Fa (active hours) | 0.8 |  |  | ERF50: Evaporation rate factor, non-active hours | 0.048 | lbm/h*ft^2 | ERF50 |  | 20 | Active | 1 | 1
Fa (inactive hours) | 0.5 |  |  | ER: Evaporation rate, non-active hours | 27.552 | lbm/h |  |  | 21 | Active | 1 | 1
[9 empty] | 22 | Inactive | 0.80639 | 0.83333
wp: Evaporated water (active hours) | 34.201 | lbm/h | Equation (2) | [5 empty] | 23 | Inactive | 0.80639 | 0.83333
wp: Evaporated water (inactive hours) | 27.5794 | lbm/h | Equation (2) | [5 empty] | 24 | Inactive | 0.80639 | 0.83333
[8 empty] | Deviation from ASHRAE |  |  | ) | )
Qp: Latent cooling load (active hours) | 35843.6729 | Btu/h |  | Qp: Latent cooling load, active hours | 34650.3871 | Btu/h |  | 3.329% |  |  | .. | ..
Qp: Latent cooling load (inactive hours) | 28904.0557 | Btu/h |  | Qp: Latent cooling load, non-active hours | 28875.3226 | Btu/h |  | 0.09941%
Pool make-up water load on DHW heater |  |  |  | Pool make-up water load on DHW heater
Pool make-up, active hours | 0.068429 | GPM |  | Pool make-up, active hours | 0.066151 | GPM
Pool make-up, inactive hours | 0.055181 | GPM |  | Pool make-up, inactive hours | 0.055126 | GPM
Hot water flow, active hours | 0.021736 | GPM | Parameter name | Hot water flow, active hours | 0.021013 | GPM |  | 3.329%
Hot water flow, inactive hours | 0.017528 | GPM |  | Hot water flow, inactive hours | 0.017511 | GPM |  | 0.09941%
Required heater output | 0.92534 | kBtu/h |  | Required heater output | 0.89454 | kBtu/h |  | 3.329%
Note on B9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pool water temperature = 80F
Note on A12: Filip Stoian: water coming into the building. This should be the average ground water temperature for the location
Note on A21: Filip Stoian: saturation vapor pressure taken at surface water temperature, in. Hg
Note on B21: Filip Stoian: Twater = 80F, RH = 100%
Note on A22: Filip Stoian: saturation pressure at room air dew point, in. Hg
Note on B22: Filip Stoian: Tair = 82F, RH = 60% Tdew = 66.8F
Note on A23: Filip Stoian: saturation pressure at room air dew point, in. Hg
Note on B23: Filip Stoian: Tair = 82F, RH = 50% Tdew = 61.59F

## Matching Summary
School Information
School Name
Address
Building Type
Number of Stories
Submission
Template Used
Date
Billing/Modeling Information
Billing Year |  | 2019
Weather File |  | JFK 2019 TMY3
Existing Electric Bills? |  | Yes
Existing Gas Bills? |  | No
Existing Steam Bills? |  | No
Existing Fuel Oil Bills? |  | No
Other Energy Source Billed? |  | No | Type?
Results
|  | Percentage | Applicable for compliance? | Maximum for compliance
Electric Usage | CVRMSE | 0% | Yes | 15% | Yes
Electric Usage | NMBE | 0% | Yes | ± 5.00% | CVRMSE
Electric Demand | CVRMSE | 0% | Yes | 15%
Electric Demand | NMBE | 0% | Yes | ± 5.00%
Gas Usage | CVRMSE | 0% | No | N/A
Gas Usage | NMBE | 0% | No | N/A
Steam Usage | CVRMSE | 0% | No | N/A
Steam Usage | NMBE | 0% | No | N/A
Fuel Oil Usage | CVRMSE | 0% | No | N/A
Fuel Oil Usage | NMBE | 0% | No | N/A
N/A | CVRMSE | 0% | No | N/A
N/A | NMBE | 0% | No | N/A
Complies? |  | Yes

## Electric Matching
|  |  | Historical Billed Usage |  |  | Existing Building Model Usage
Month |  | Billing Period | Electric Usage (kwh) | Electric Demand (kW) | Electric Cost | Electric Usage (kwh) | Electric Demand (kW) | Electric Cost | Electric Usage % Difference | Electric Demand % Difference | Electric Cost % Difference
Jan |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Feb |  | 28 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Mar |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Apr |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
May |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jun |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jul |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Aug |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Sep |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Oct |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Nov |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Dec |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
TOTAL |  | 365 | 12 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | #DIV/0!
Error in Modeled Bills | [5 empty] | Error in Modeled Bills
Month | Billing Period | KWh Usage | KW Demand | Cost |  | Month | Billing Period | KWh Usage | KW Demand | Cost
Jan | 31 | 0 | 0 | 0 |  | Jan | 31 | 0% | 0% | #DIV/0!
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0% | 0% | #DIV/0!
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0% | 0% | #DIV/0!
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0% | 0% | #DIV/0!
May | 31 | 0 | 0 | 0 |  | May | 31 | 0% | 0% | #DIV/0!
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0% | 0% | #DIV/0!
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0% | 0% | #DIV/0!
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0% | 0% | #DIV/0!
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0% | 0% | #DIV/0!
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0% | 0% | #DIV/0!
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0% | 0% | #DIV/0!
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0% | 0% | #DIV/0!
| 365 | 0 | 0 | 0 |  |  | 365 | 0% | 0% | #DIV/0!
CVRMSE (<= 15%) | [5 empty] | NMBE (<= 5%, >= -5%)
Month | Billing Period | KWh (y-y')^2 | KW (y-y')^2 | Cost (y-y')^2 |  | Month | Billing Period | KWh (y-y') | KW (y-y') | Cost (y-y')
Jan | 31 | 0 | 0 | 0 |  | Jan | 31 | 0 | 0 | 0
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0 | 0 | 0
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0 | 0 | 0
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0 | 0 | 0
May | 31 | 0 | 0 | 0 |  | May | 31 | 0 | 0 | 0
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0 | 0 | 0
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0 | 0 | 0
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0 | 0 | 0
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0 | 0 | 0
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0 | 0 | 0
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0 | 0 | 0
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0 | 0 | 0
CVRMSE |  | 0% | 0% | #DIV/0! |  | NMBE |  | 0% | 0% | #DIV/0!

## Gas Matching
|  |  | Historical Billed Usage |  |  | Existing Building Model Usage
Month |  | Billing Period | Gas Usage (Therm) | Gas Demand (kBTU/hr) | Gas Cost | Gas Usage (Therm) | Gas Demand (kBTU/hr) | Gas Cost | Gas Usage % Difference | Gas Demand % Difference | Gas Cost % Difference
Jan |  | 31 | 1 | 1 | 0 | 2 | 1 | 0 | 0.5 | 0 | #DIV/0!
Feb |  | 28 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Mar |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Apr |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
May |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jun |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jul |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Aug |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Sep |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Oct |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Nov |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Dec |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
TOTAL |  | 365 | 12 | 12 | 0 | 13 | 12 | 0 | 0.076923 | 0 | #DIV/0!
Error in Modeled Bills | [5 empty] | Error in Modeled Bills
Month | Billing Period | Gas Usage | Gas Demand | Cost |  | Month | Billing Period | Gas Usage | Gas Demand | Cost
Jan | 31 | 1 | 0 | 0 |  | Jan | 31 | 100% | 0% | #DIV/0!
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0% | 0% | #DIV/0!
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0% | 0% | #DIV/0!
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0% | 0% | #DIV/0!
May | 31 | 0 | 0 | 0 |  | May | 31 | 0% | 0% | #DIV/0!
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0% | 0% | #DIV/0!
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0% | 0% | #DIV/0!
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0% | 0% | #DIV/0!
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0% | 0% | #DIV/0!
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0% | 0% | #DIV/0!
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0% | 0% | #DIV/0!
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0% | 0% | #DIV/0!
| 365 | 1 | 0 | 0 |  |  | 365 | 8.333% | 0% | #DIV/0!
CVRMSE (<= 15%) | [5 empty] | NMBE (<= 5%, >= -5%)
Month | Billing Period | Therm (y-y')^2 | kBTU/hr (y-y')^2 | Cost (y-y')^2 |  | Month | Billing Period | Therm (y-y') | kBTU/hr (y-y') | Cost (y-y')
Jan | 31 | 1 | 0 | 0 |  | Jan | 31 | 1 | 0 | 0
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0 | 0 | 0
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0 | 0 | 0
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0 | 0 | 0
May | 31 | 0 | 0 | 0 |  | May | 31 | 0 | 0 | 0
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0 | 0 | 0
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0 | 0 | 0
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0 | 0 | 0
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0 | 0 | 0
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0 | 0 | 0
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0 | 0 | 0
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0 | 0 | 0
CVRMSE |  | 30.15% | 0% | #DIV/0! |  | NMBE |  | 9.091% | 0% | #DIV/0!

## Steam Matching
|  |  | Historical Billed Usage |  |  | Existing Building Model Usage
Month |  | Billing Period | Steam Usage (Therm) | Steam Demand (kBTU/hr) | Steam Cost | Steam Usage (Therm) | Steam Demand (kBTU/hr) | Steam Cost | Steam Usage % Difference | Steam Demand % Difference | Steam Cost % Difference
Jan |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Feb |  | 28 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Mar |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Apr |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
May |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jun |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jul |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Aug |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Sep |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Oct |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Nov |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Dec |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
TOTAL |  | 365 | 12 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | #DIV/0!
Error in Modeled Bills | [5 empty] | Error in Modeled Bills (Percentage)
Month | Billing Period | Steam Usage | Steam Demand | Cost |  | Month | Billing Period | Steam Usage | Steam Demand | Cost
Jan | 31 | 0 | 0 | 0 |  | Jan | 31 | 0% | 0% | #DIV/0!
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0% | 0% | #DIV/0!
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0% | 0% | #DIV/0!
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0% | 0% | #DIV/0!
May | 31 | 0 | 0 | 0 |  | May | 31 | 0% | 0% | #DIV/0!
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0% | 0% | #DIV/0!
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0% | 0% | #DIV/0!
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0% | 0% | #DIV/0!
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0% | 0% | #DIV/0!
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0% | 0% | #DIV/0!
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0% | 0% | #DIV/0!
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0% | 0% | #DIV/0!
| 365 | 0 | 0 | 0 |  |  | 365 | 0% | 0% | #DIV/0!
CVRMSE (<= 15%) | [5 empty] | NMBE (<= 5%, >= -5%)
Month | Billing Period | Therm (y-y')^2 | kBTU/hr (y-y')^2 | Cost (y-y')^2 |  | Month | Billing Period | Therm (y-y') | kBTU/hr (y-y') | Cost (y-y')
Jan | 31 | 0 | 0 | 0 |  | Jan | 31 | 0 | 0 | 0
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0 | 0 | 0
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0 | 0 | 0
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0 | 0 | 0
May | 31 | 0 | 0 | 0 |  | May | 31 | 0 | 0 | 0
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0 | 0 | 0
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0 | 0 | 0
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0 | 0 | 0
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0 | 0 | 0
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0 | 0 | 0
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0 | 0 | 0
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0 | 0 | 0
CVRMSE |  | 0% | 0% | #DIV/0! |  | NMBE |  | 0% | 0% | #DIV/0!

## Fuel Oil Matching
|  |  | Historical Billed Usage |  |  | Existing Building Model Usage
Month |  | Billing Period | Fuel Oil Usage (mBTU) | Demand (kBTU/hr) | Fuel Oil Cost | Fuel Oil Usage (mBTU) | Demand (kBTU/hr) | Fuel Oil Cost | Fuel Oil Usage % Difference | Fuel Oil Demand % Difference | Fuel Oil Cost % Difference
Jan |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Feb |  | 28 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Mar |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Apr |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
May |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jun |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jul |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Aug |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Sep |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Oct |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Nov |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Dec |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
TOTAL |  | 365 | 12 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | #DIV/0!
Error in Modeled Bills | [5 empty] | Error in Modeled Bills
Month | Billing Period | Fuel Oil Usage | Fuel Oil Demand | Cost |  | Month | Billing Period | Fuel Oil Usage | Fuel Oil Demand | Cost
Jan | 31 | 0 | 0 | 0 |  | Jan | 31 | 0% | 0% | #DIV/0!
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0% | 0% | #DIV/0!
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0% | 0% | #DIV/0!
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0% | 0% | #DIV/0!
May | 31 | 0 | 0 | 0 |  | May | 31 | 0% | 0% | #DIV/0!
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0% | 0% | #DIV/0!
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0% | 0% | #DIV/0!
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0% | 0% | #DIV/0!
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0% | 0% | #DIV/0!
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0% | 0% | #DIV/0!
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0% | 0% | #DIV/0!
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0% | 0% | #DIV/0!
| 365 | 0 | 0 | 0 |  |  | 365 | 0% | 0% | #DIV/0!
CVRMSE (<= 15%) | [5 empty] | NMBE (<= 5%, >= -5%)
Month | Billing Period | Therm (y-y')^2 | kBTU/hr (y-y')^2 | Cost (y-y')^2 |  | Month | Billing Period | Therm (y-y') | kBTU/hr (y-y') | Cost (y-y')
Jan | 31 | 0 | 0 | 0 |  | Jan | 31 | 0 | 0 | 0
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0 | 0 | 0
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0 | 0 | 0
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0 | 0 | 0
May | 31 | 0 | 0 | 0 |  | May | 31 | 0 | 0 | 0
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0 | 0 | 0
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0 | 0 | 0
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0 | 0 | 0
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0 | 0 | 0
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0 | 0 | 0
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0 | 0 | 0
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0 | 0 | 0
CVRMSE |  | 0% | 0% | #DIV/0! |  | NMBE |  | 0% | 0% | #DIV/0!

## Other Energy Matching
|  |  | Historical Billed Usage |  |  | Existing Building Model Usage
Month |  | Billing Period | Energy Usage (mBTU) | Energy Demand (kBTU/hr) | Energy Cost | Energy Usage (mBTU) | Energy Demand (kBTU/hr) | Energy Cost | Energy Usage % Difference | Energy Demand % Difference | Energy Cost % Difference
Jan |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Feb |  | 28 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Mar |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Apr |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
May |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jun |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Jul |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Aug |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Sep |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Oct |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Nov |  | 30 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
Dec |  | 31 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | #DIV/0!
TOTAL |  | 365 | 12 | 12 | 0 | 12 | 12 | 0 | 0 | 0 | #DIV/0!
Error in Modeled Bills | [5 empty] | Error in Modeled Bills
Month | Billing Period | Energy Usage | Energy Demand | Energy Cost |  | Month | Billing Period | Energy Usage | Energy Demand | Energy Cost
Jan | 31 | 0 | 0 | 0 |  | Jan | 31 | 0% | 0% | #DIV/0!
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0% | 0% | #DIV/0!
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0% | 0% | #DIV/0!
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0% | 0% | #DIV/0!
May | 31 | 0 | 0 | 0 |  | May | 31 | 0% | 0% | #DIV/0!
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0% | 0% | #DIV/0!
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0% | 0% | #DIV/0!
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0% | 0% | #DIV/0!
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0% | 0% | #DIV/0!
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0% | 0% | #DIV/0!
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0% | 0% | #DIV/0!
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0% | 0% | #DIV/0!
| 365 | 0 | 0 | 0 |  |  | 365 | 0% | 0% | #DIV/0!
CVRMSE (<= 15%) | [5 empty] | NMBE (<= 5%, >= -5%)
Month | Billing Period | Therm (y-y')^2 | kBTU/hr (y-y')^2 | Cost (y-y')^2 |  | Month | Billing Period | Therm (y-y') | kBTU/hr (y-y') | Cost (y-y')
Jan | 31 | 0 | 0 | 0 |  | Jan | 31 | 0 | 0 | 0
Feb | 28 | 0 | 0 | 0 |  | Feb | 28 | 0 | 0 | 0
Mar | 31 | 0 | 0 | 0 |  | Mar | 31 | 0 | 0 | 0
Apr | 30 | 0 | 0 | 0 |  | Apr | 30 | 0 | 0 | 0
May | 31 | 0 | 0 | 0 |  | May | 31 | 0 | 0 | 0
Jun | 30 | 0 | 0 | 0 |  | Jun | 30 | 0 | 0 | 0
Jul | 31 | 0 | 0 | 0 |  | Jul | 31 | 0 | 0 | 0
Aug | 31 | 0 | 0 | 0 |  | Aug | 31 | 0 | 0 | 0
Sep | 30 | 0 | 0 | 0 |  | Sep | 30 | 0 | 0 | 0
Oct | 31 | 0 | 0 | 0 |  | Oct | 31 | 0 | 0 | 0
Nov | 30 | 0 | 0 | 0 |  | Nov | 30 | 0 | 0 | 0
Dec | 31 | 0 | 0 | 0 |  | Dec | 31 | 0 | 0 | 0
CVRMSE |  | 0% | 0% | #DIV/0! |  | NMBE |  | 0% | 0% | #DIV/0!